## tb_entry_breakdown (1)
WTG's Down Time
Customer | Date | State | Site | Location No. | Feeder | Stop Due To | Stop From | Stop To | Total Stop | Reason | Alarm | Alarm Description | Action Taken
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 15:17 | 15:21 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 15:37 | 15:39 | 0:02 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 15:58 | 20:10 | 4:12 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 12:51 | 15:54 | 3:03 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for KPTCL team 11KV line jumper opening work
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 11:00 | 11:03 | 0:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV01 | 1 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 16:28 | 16:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 17:29 | 17:33 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 19:17 | 20:50 | 1:33 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV01 | 1 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV01 | 1 | WTG | 3:40 | 3:48 | 0:08 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 21:40 | 21:56 | 0:16 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 22:27 | 22:35 | 0:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 23:06 | 23:59 | 0:53 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV01 | 1 | WTG | 0:00 | 7:50 | 7:50 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Grid isolated due to LT line crossing issue
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 17:19 | 18:42 | 1:23 | Feeder tripped E/F | IG01 | Internal shutdown | LT line crossing sag arrest work
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV01 | 1 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 12:40 | 12:50 | 0:10 | Internal Shutdown | IG01 | Internal shutdown | LC taken by HESCOM Line work
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV01 | 1 | WTG | 13:00 | 13:04 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 10:15 | 10:19 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 11:20 | 11:37 | 0:17 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 13:29 | 13:58 | 0:29 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 15:09 | 15:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV01 | 1 | WTG | 20:27 | 20:31 | 0:04 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 22:28 | 23:59 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV01 | 1 | WTG | 0:00 | 7:20 | 7:20 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | 33kv line fault
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 14:09 | 18:55 | 4:46 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for 33kv line tree trimming work
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 1:21 | 1:28 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 9:33 | 17:03 | 7:30 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for LC taken by line maintenence tree cutting work
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 15:14 | 15:22 | 0:08 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV01 | 1 | FORCE MAJEURE | 17:17 | 18:03 | 0:46 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 17:23 | 18:15 | 0:52 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV01 | 1 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV01 | 1 | FORCE MAJEURE | 18:02 | 18:06 | 0:04 | Covid 19 | 31013 | Blade bearing lubrication is in maintenance state. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV01 | 1 | FORCE MAJEURE | 17:10 | 24:00 | 6:50 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV01 | 1 | FORCE MAJEURE | 0:00 | 8:40 | 8:40 | Covid 19 |  |  | Replaced PTAI216 module and reset start wtg
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 12:36 | 13:20 | 0:44 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for Tawar Sir KPTCL Work
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 18:34 | 18:44 | 0:10 | Feeder tripped E/F |  |  | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV01 | 1 | GA INT | 8:34 | 9:59 | 1:25 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for BBV02 jumper opening work
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV01 | 1 | WTG | 0:00 | 23:00 | 23:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | 33Kv Jumper work completed
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 15:17 | 15:17 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 15:17 | 15:21 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 15:21 | 15:58 | 0:37 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 15:37 | 15:39 | 0:02 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 15:58 | 20:10 | 4:12 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 20:10 | 24:00 | 3:50 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-07 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 12:51 | 12:51 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 12:51 | 15:54 | 3:03 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for KPTCL team 11KV line jumper opening work
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 15:54 | 24:00 | 8:06 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 11:00 | 11:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 11:00 | 11:03 | 0:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 11:03 | 23:59 | 12:56 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 5:54 | 5:54 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV02 | 1 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 7:14 | 16:28 | 9:14 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 16:28 | 16:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 16:34 | 17:29 | 0:55 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 17:29 | 24:00 | 6:31 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 19:17 | 19:17 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 19:17 | 20:50 | 1:33 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 20:50 | 24:00 | 3:10 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 16:04 | 16:04 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV02 | 1 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 17:04 | 23:59 | 6:55 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 21:40 | 21:40 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 21:40 | 21:56 | 0:16 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 21:56 | 22:27 | 0:31 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 22:27 | 22:35 | 0:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 22:35 | 23:59 | 1:24 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 23:06 | 23:59 | 0:53 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 7:50 | 7:50 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Grid isolated due to LT line crossing issue
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 7:50 | 17:19 | 9:29 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 17:19 | 18:42 | 1:23 | Feeder tripped E/F | IG01 | Internal shutdown | LT line crossing sag arrest work
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 18:42 | 23:59 | 5:17 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 12:40 | 12:40 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV02 | 1 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 7:05 | 23:59 | 16:54 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 12:40 | 12:50 | 0:10 | Internal Shutdown | IG01 | Internal shutdown | LC taken by HESCOM Line work
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 12:50 | 23:59 | 11:09 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 10:15 | 10:15 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 10:15 | 10:19 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 10:19 | 11:15 | 0:56 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 11:20 | 11:37 | 0:17 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 11:37 | 23:59 | 12:22 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 12:50 | 23:59 | 11:09 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 13:29 | 13:29 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 13:29 | 13:58 | 0:29 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 13:58 | 15:09 | 1:11 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 15:09 | 15:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 15:29 | 23:59 | 8:30 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-24 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 22:28 | 22:28 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 22:28 | 23:59 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 22:34 | 23:59 | 1:25 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 7:20 | 7:20 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 7:20 | 14:09 | 6:49 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 14:09 | 18:55 | 4:46 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for 33kv line tree trimming work
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 18:55 | 24:00 | 5:05 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 1:21 | 1:21 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 1:21 | 1:28 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 1:28 | 9:33 | 8:05 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 9:33 | 17:03 | 7:30 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for LC taken by line maintenence tree cutting work
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 17:03 | 24:00 | 6:57 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 15:14 | 15:14 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 15:14 | 15:22 | 0:08 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 15:22 | 24:00 | 8:38 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | 23009 | Hub healthcheck alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | 23009 | Hub healthcheck alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 17:23 | 17:23 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 17:23 | 18:15 | 0:52 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV02 | 1 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 18:58 | 24:00 | 5:02 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 | 23009 | Hub healthcheck alarm. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | 23009 | Hub healthcheck alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 12:36 | 12:36 | Covid 19 | 7676 | Generator side hardware detected over-current Fault phase B. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 12:36 | 13:20 | 0:44 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for Tawar Sir KPTCL Work
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 13:20 | 18:34 | 5:14 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 18:34 | 18:44 | 0:10 | Feeder tripped E/F |  |  | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 18:44 | 24:00 | 5:16 | Covid 19 | 26001 | All tower-vibration sensors in drivetrain direction defective | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 | 23009 | Hub healthcheck alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 8:34 | 8:34 | Covid 19 | 23009 | Hub healthcheck alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV02 | 1 | GA INT | 8:34 | 9:59 | 1:25 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for BBV02 jumper opening work
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 9:59 | 23:59 | 14:00 | Covid 19 | 23009 | Hub healthcheck alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | IG01 | Internal shutdown | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV02 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | 23009 | Hub healthcheck alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-20 | Karnataka | Bagewadi | BBV02 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Gearbox issue
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 9:37 | 9:49 | 0:12 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 15:17 | 15:21 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 15:37 | 15:39 | 0:02 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 15:58 | 20:10 | 4:12 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 20:18 | 20:22 | 0:04 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 12:51 | 15:54 | 3:03 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for KPTCL team 11KV line jumper opening work
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 11:00 | 11:03 | 0:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV03 | 1 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 14:55 | 15:10 | 0:15 | Breakdown Maintenance | 7786 |  | Reboot the wtg and started
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 16:28 | 16:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 17:29 | 19:18 | 1:49 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reboot the wtg and started
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 19:17 | 20:50 | 1:33 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 1:28 | 2:04 | 0:36 | Breakdown Maintenance | 28017 | Generator cooling slipring fan overload switch 1 is open/tripped. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 0:12 | 0:16 | 0:04 | Breakdown Maintenance | 12105 | Blade 3: IPS was active in wrong area. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 21:17 | 21:29 | 0:12 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 2:04 | 2:54 | 0:50 | Breakdown Maintenance | 28017 | Generator cooling slipring fan overload switch 1 is open/tripped. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV03 | 1 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 21:40 | 21:56 | 0:16 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 22:27 | 22:35 | 0:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 23:06 | 23:59 | 0:53 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 0:00 | 7:50 | 7:50 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Grid isolated due to LT line crossing issue
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 7:50 | 8:45 | 0:55 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 15:13 | 16:35 | 1:22 | Breakdown Maintenance |  |  | Ms for repetative error work
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 17:19 | 18:42 | 1:23 | Feeder tripped E/F | IG01 | Internal shutdown | LT line crossing sag arrest work
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV03 | 1 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 12:40 | 12:50 | 0:10 | Internal Shutdown | IG01 | Internal shutdown | LC taken by HESCOM Line work
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 12:56 | 13:06 | 0:10 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 10:15 | 10:19 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 11:20 | 11:37 | 0:17 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 13:29 | 13:58 | 0:29 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 15:09 | 15:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 22:28 | 23:59 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 0:00 | 7:20 | 7:20 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | 33kv line fault
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 14:09 | 18:55 | 4:46 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for 33kv line tree trimming work
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 1:21 | 1:28 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 9:33 | 17:03 | 7:30 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for LC taken by line maintenence tree cutting work
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 16:52 | 16:56 | 0:04 | Breakdown Maintenance | 7786 |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 15:14 | 15:22 | 0:08 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 14:38 | 14:42 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 17:08 | 17:27 | 0:19 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV03 | 1 | FORCE MAJEURE | 17:45 | 17:49 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 17:23 | 18:15 | 0:52 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV03 | 1 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV03 | 1 | FORCE MAJEURE | 20:10 | 24:00 | 3:50 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV03 | 1 | FORCE MAJEURE | 0:00 | 2:13 | 2:13 | Covid 19 | 4018 | Stator breaker failed in closing when demanded to close. | Found spring change motor failure then new replaced and reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV03 | 1 | FORCE MAJEURE | 12:21 | 12:29 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV03 | 1 | FORCE MAJEURE | 12:44 | 12:57 | 0:13 | Covid 19 |  |  | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV03 | 1 | FORCE MAJEURE | 14:18 | 24:00 | 9:42 | Covid 19 | 4018 | Stator breaker failed in closing when demanded to close. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV03 | 1 | FORCE MAJEURE | 0:00 | 20:45 | 20:45 | Covid 19 | 11020 | Grid frequency from converter below operation range. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 12:36 | 13:20 | 0:44 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for Tawar Sir KPTCL Work
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 18:34 | 18:44 | 0:10 | Feeder tripped E/F |  |  | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 13:52 | 14:04 | 0:12 | Breakdown Maintenance | 7786 |  | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV03 | 1 | GA INT | 8:34 | 9:59 | 1:25 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for BBV02 jumper opening work
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 13:44 | 13:52 | 0:08 | Breakdown Maintenance | 7786 |  | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV03 | 1 | WTG | 18:32 | 23:00 | 4:28 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Mannully stopped BBV01 jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 13:50 | 13:54 | 0:04 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 15:17 | 15:21 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 15:37 | 15:39 | 0:02 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 15:58 | 20:10 | 4:12 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 4:23 | 4:32 | 0:09 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 14:32 | 14:40 | 0:08 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 8:14 | 8:26 | 0:12 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 21:02 | 21:06 | 0:04 | Breakdown Maintenance | 26009 | Offset of the tower-vibration sensor in drivetrain direction above error limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 12:51 | 15:54 | 3:03 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for KPTCL team 11KV line jumper opening work
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 16:17 | 16:29 | 0:12 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 16:34 | 16:38 | 0:04 | Breakdown Maintenance | 30006 | Nacelle rotation overspeed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 0:59 | 1:03 | 0:04 | Breakdown Maintenance | 30006 | Nacelle rotation overspeed. | auto reset
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 11:00 | 11:03 | 0:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 16:30 | 16:34 | 0:04 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | auto reset
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV10 | 1 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 16:28 | 16:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 17:29 | 17:33 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 12:05 | 12:09 | 0:04 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 19:17 | 20:50 | 1:33 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 14:41 | 14:45 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 16:32 | 16:36 | 0:04 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 6:52 | 7:02 | 0:10 | Breakdown Maintenance | 26015 | Tower vibration (acceleration peak-to-peak value) in drivetrain direction delayed is above limit | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 12:34 | 12:38 | 0:04 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 14:40 | 14:44 | 0:04 | Breakdown Maintenance | 30006 | Nacelle rotation overspeed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV10 | 1 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 17:26 | 17:30 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 21:40 | 21:56 | 0:16 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 22:27 | 22:35 | 0:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 23:06 | 23:59 | 0:53 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 0:00 | 7:50 | 7:50 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Grid isolated due to LT line crossing issue
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 17:19 | 18:42 | 1:23 | Feeder tripped E/F | IG01 | Internal shutdown | LT line crossing sag arrest work
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 12:41 | 12:49 | 0:08 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV10 | 1 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 12:40 | 12:50 | 0:10 | Internal Shutdown | IG01 | Internal shutdown | LC taken by HESCOM Line work
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 10:15 | 10:19 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 11:20 | 11:37 | 0:17 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 14:55 | 15:03 | 0:08 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 13:29 | 13:58 | 0:29 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 15:09 | 15:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 17:12 | 17:16 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 12:38 | 12:42 | 0:04 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 22:28 | 23:59 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 0:00 | 7:20 | 7:20 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | 33kv line fault
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 14:09 | 18:55 | 4:46 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for 33kv line tree trimming work
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 1:21 | 1:28 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 9:33 | 17:03 | 7:30 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for LC taken by line maintenence tree cutting work
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 18:41 | 18:49 | 0:08 | Breakdown Maintenance | 24001 | Drive train swinging. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 15:14 | 15:22 | 0:08 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 18:03 | 18:07 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 8:41 | 8:45 | 0:04 | Breakdown Maintenance | 26017 | More than 3 tower-vibration (acceleration peak-peak) warnings within specified time | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 10:15 | 10:19 | 0:04 | Breakdown Maintenance | 26015 | Tower vibration (acceleration peak-to-peak value) in drivetrain direction delayed is above limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 21:36 | 21:40 | 0:04 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 14:26 | 14:30 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 16:40 | 16:44 | 0:04 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 19:06 | 19:10 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 15:41 | 15:45 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 11:09 | 11:13 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 17:23 | 18:15 | 0:52 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV10 | 1 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 22:00 | 22:04 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 15:30 | 15:50 | 0:20 | Covid 19 | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 16:54 | 17:02 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 17:38 | 17:42 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 19:34 | 19:38 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 8:50 | 9:02 | 0:12 | Covid 19 |  |  | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 17:30 | 17:58 | 0:28 | Covid 19 |  |  | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV10 | 1 | FORCE MAJEURE | 21:40 | 21:44 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 15:27 | 15:51 | 0:24 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 12:36 | 13:20 | 0:44 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for Tawar Sir KPTCL Work
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 18:34 | 18:44 | 0:10 | Feeder tripped E/F |  |  | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 8:26 | 9:15 | 0:49 | Breakdown Maintenance | 30006 | Nacelle rotation overspeed. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV10 | 1 | GA INT | 8:34 | 9:59 | 1:25 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for BBV02 jumper opening work
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 12:34 | 13:10 | 0:36 | Breakdown Maintenance | 30006 | Nacelle rotation overspeed. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 15:57 | 16:22 | 0:25 | Breakdown Maintenance | 4031 | External diode temperature above error limit. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 12:10 | 13:22 | 1:12 | Breakdown Maintenance | 9067 | Gearbox oil cooling fan 1 overload switch failure. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 18:32 | 23:11 | 4:39 | Breakdown Maintenance | 12026 | Hub grid fuse has opened. | Mannully stopped BBV01 jumper connection work
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 0:37 | 1:05 | 0:28 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 1:09 | 1:26 | 0:17 | Breakdown Maintenance | 26017 | More than 3 tower-vibration (acceleration peak-peak) warnings within specified time | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 13:41 | 13:45 | 0:04 | Breakdown Maintenance | 30006 | Nacelle rotation overspeed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV10 | 1 | WTG | 15:57 | 16:01 | 0:04 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 15:17 | 15:17 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 15:17 | 15:21 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 15:21 | 15:58 | 0:37 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 15:37 | 15:39 | 0:02 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 15:58 | 20:10 | 4:12 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 20:10 | 24:00 | 3:50 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-07 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 12:51 | 12:51 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 12:51 | 15:54 | 3:03 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for KPTCL team 11KV line jumper opening work
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 15:54 | 24:00 | 8:06 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 11:00 | 11:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 11:00 | 11:03 | 0:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 11:03 | 23:59 | 12:56 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 5:54 | 5:54 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV12 | 1 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 7:14 | 16:28 | 9:14 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 16:28 | 16:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 16:34 | 17:29 | 0:55 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 17:29 | 24:00 | 6:31 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 19:17 | 19:17 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 19:17 | 20:50 | 1:33 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 20:50 | 24:00 | 3:10 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 16:04 | 16:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV12 | 1 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 17:04 | 23:59 | 6:55 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 21:40 | 21:40 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 21:40 | 21:56 | 0:16 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 21:56 | 22:27 | 0:31 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 22:27 | 22:35 | 0:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 22:35 | 23:59 | 1:24 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 23:06 | 23:59 | 0:53 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 7:50 | 7:50 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Grid isolated due to LT line crossing issue
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 7:50 | 17:19 | 9:29 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 17:19 | 18:42 | 1:23 | Feeder tripped E/F | IG01 | Internal shutdown | LT line crossing sag arrest work
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 18:42 | 23:59 | 5:17 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 12:40 | 12:40 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV12 | 1 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 7:05 | 23:59 | 16:54 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 12:40 | 12:50 | 0:10 | Internal Shutdown | IG01 | Internal shutdown | LC taken by HESCOM Line work
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 12:50 | 23:59 | 11:09 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 10:15 | 10:15 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 10:15 | 10:19 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 10:19 | 11:15 | 0:56 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 11:20 | 11:37 | 0:17 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 11:37 | 23:59 | 12:22 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 13:29 | 13:29 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 13:29 | 13:58 | 0:29 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 13:58 | 15:09 | 1:11 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 15:09 | 15:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 15:29 | 23:59 | 8:30 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-24 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 22:28 | 22:28 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 22:28 | 23:59 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 22:34 | 23:59 | 1:25 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 14:09 | 14:09 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 14:09 | 18:55 | 4:46 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for 33kv line tree trimming work
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 18:55 | 24:00 | 5:05 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 1:21 | 1:21 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 1:21 | 1:28 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 1:28 | 9:33 | 8:05 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 9:33 | 17:03 | 7:30 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for LC taken by line maintenence tree cutting work
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 17:03 | 24:00 | 6:57 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 15:14 | 15:14 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 15:14 | 15:22 | 0:08 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 15:22 | 24:00 | 8:38 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 17:23 | 17:23 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 17:23 | 18:15 | 0:52 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV12 | 1 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 18:58 | 24:00 | 5:02 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 12:36 | 12:36 | Covid 19 | 23007 | Converter healthcheck alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 12:36 | 13:20 | 0:44 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for Tawar Sir KPTCL Work
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 13:20 | 18:34 | 5:14 | Covid 19 | 26001 | All tower-vibration sensors in drivetrain direction defective | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 18:34 | 18:44 | 0:10 | Feeder tripped E/F |  |  | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 18:44 | 24:00 | 5:16 | Covid 19 | 26001 | All tower-vibration sensors in drivetrain direction defective | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 8:34 | 8:34 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV12 | 1 | GA INT | 8:34 | 9:59 | 1:25 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for BBV02 jumper opening work
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 9:59 | 23:59 | 14:00 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | 9010 | Gearbox main bearing temperature 2 above error limit. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV12 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-20 | Karnataka | Bagewadi | BBV12 | 1 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Generator failure
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 5:49 | 5:57 | 0:08 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 20:25 | 20:34 | 0:09 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 15:17 | 15:21 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 15:37 | 15:39 | 0:02 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 15:58 | 20:10 | 4:12 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 11:36 | 11:44 | 0:08 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 19:57 | 20:01 | 0:04 | Breakdown Maintenance | 1001 | Anemometer 1 fuse error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 11:41 | 11:49 | 0:08 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 12:51 | 15:54 | 3:03 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for KPTCL team 11KV line jumper opening work
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 16:33 | 16:41 | 0:08 | Breakdown Maintenance | 12006 | Health check error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 11:00 | 11:03 | 0:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV13 | 1 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 11:40 | 13:03 | 1:23 | Breakdown Maintenance | 7613 | Converter system communication handshake fault. | Checked and reboot the wtg and started
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 16:28 | 16:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 17:29 | 17:33 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 18:59 | 20:28 | 1:29 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Checked and reboot the wtg and started
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 5:09 | 5:26 | 0:17 | Breakdown Maintenance | 33014 | Customer alarm 15 | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 19:17 | 20:50 | 1:33 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 1:50 | 1:54 | 0:04 | Breakdown Maintenance | 4031 | External diode temperature above error limit. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 2:23 | 2:45 | 0:22 | Breakdown Maintenance | 10044 | Generator grounding brush worn error. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 8:35 | 9:39 | 1:04 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 20:51 | 21:11 | 0:20 | Breakdown Maintenance | 1001 | Anemometer 1 fuse error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 11:17 | 11:21 | 0:04 | Breakdown Maintenance | 33014 | Customer alarm 15 | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV13 | 1 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 21:40 | 21:56 | 0:16 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 22:27 | 22:35 | 0:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 23:06 | 23:59 | 0:53 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped due to overcurrent fault
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 0:00 | 7:50 | 7:50 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Grid isolated due to LT line crossing issue
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 9:51 | 9:59 | 0:08 | Breakdown Maintenance | 33014 | Customer alarm 15 | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 17:19 | 18:42 | 1:23 | Feeder tripped E/F | IG01 | Internal shutdown | LT line crossing sag arrest work
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV13 | 1 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 12:40 | 12:50 | 0:10 | Internal Shutdown | IG01 | Internal shutdown | LC taken by HESCOM Line work
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 4:58 | 5:02 | 0:04 | Breakdown Maintenance | 4031 | External diode temperature above error limit. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 10:15 | 10:19 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 11:20 | 11:37 | 0:17 | Feeder tripped E/F | IG02 | Earth Fault | Feedere tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 13:29 | 13:58 | 0:29 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 15:09 | 15:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 22:28 | 23:59 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 0:00 | 7:20 | 7:20 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | 33kv line fault
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 14:09 | 18:55 | 4:46 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for 33kv line tree trimming work
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 1:21 | 1:28 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 9:33 | 17:03 | 7:30 | Internal Shutdown | IG01 | Internal shutdown | Manual stop for LC taken by line maintenence tree cutting work
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 19:50 | 19:54 | 0:04 | Breakdown Maintenance | 33014 | Customer alarm 15 | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 16:08 | 16:23 | 0:15 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 21:18 | 21:22 | 0:04 | Breakdown Maintenance | 10044 | Generator grounding brush worn error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 12:55 | 12:59 | 0:04 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 5:42 | 5:46 | 0:04 | Breakdown Maintenance | 4031 | External diode temperature above error limit. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 15:14 | 15:22 | 0:08 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 21:43 | 21:47 | 0:04 | Breakdown Maintenance | 11004 | Active power 10m filter above limit. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 2:21 | 2:25 | 0:04 | Breakdown Maintenance | 4031 | External diode temperature above error limit. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 16:38 | 16:42 | 0:04 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 14:55 | 14:59 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 16:41 | 17:10 | 0:29 | Breakdown Maintenance | 1001 | Anemometer 1 fuse error. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV13 | 1 | FORCE MAJEURE | 1:11 | 1:15 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV13 | 1 | FORCE MAJEURE | 18:36 | 18:55 | 0:19 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV13 | 1 | FORCE MAJEURE | 16:57 | 17:01 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 17:23 | 18:15 | 0:52 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV13 | 1 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV13 | 1 | FORCE MAJEURE | 16:55 | 17:03 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV13 | 1 | FORCE MAJEURE | 18:49 | 18:57 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV13 | 1 | FORCE MAJEURE | 14:18 | 14:26 | 0:08 | Covid 19 |  |  | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV13 | 1 | FORCE MAJEURE | 16:34 | 16:38 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV13 | 1 | FORCE MAJEURE | 20:29 | 20:33 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 12:36 | 13:20 | 0:44 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for Tawar Sir KPTCL Work
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 18:34 | 18:44 | 0:10 | Feeder tripped E/F |  |  | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 6:48 | 7:50 | 1:02 | Breakdown Maintenance | 14004 | Hydraulic unit oil level is too low. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV13 | 1 | GA INT | 8:34 | 9:59 | 1:25 | Internal Shutdown | IG01 | Internal shutdown | Mannully stopped for BBV02 jumper opening work
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 18:32 | 23:50 | 5:18 | Breakdown Maintenance | 10033 | Generator bearing temperature DE above error limit. | Mannully stopped BBV01 jumper connection work
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 16:41 | 16:49 | 0:08 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV13 | 1 | WTG | 22:16 | 22:20 | 0:04 | Breakdown Maintenance | 4031 | External diode temperature above error limit. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 13:24 | 13:36 | 0:12 | Breakdown Maintenance | 1023 | Wind speed difference error. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 18:14 | 18:41 | 0:27 | Breakdown Maintenance | 1024 | Wind direction difference error. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 17:09 | 17:17 | 0:08 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 17:52 | 18:00 | 0:08 | Breakdown Maintenance | 1023 | Wind speed difference error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 0:47 | 0:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 1:43 | 1:52 | 0:09 | Breakdown Maintenance | 3016 | Rotor brake is closed. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 12:11 | 12:23 | 0:12 | Breakdown Maintenance | 1023 | Wind speed difference error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 15:15 | 15:30 | 0:15 | Breakdown Maintenance | 10037 | All sensors of generator bearing temperature NDE defective (Short cut or wire break). | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 15:59 | 16:25 | 0:26 | Breakdown Maintenance | 10011 | All sensors of generator winding V temperature defective (Short cut or wire break). | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 14:15 | 14:19 | 0:04 | Breakdown Maintenance | 1023 | Wind speed difference error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV17 | 3 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 7:46 | 13:10 | 5:24 | Breakdown Maintenance | 3001 | Brake chain - fuse opened. | Check and found K65.1 relay negative voltage missing , corrected and wtg restored
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 12:45 | 13:08 | 0:23 | Internal Shutdown | IG01 | Internal shutdown | Feeder internal shut down for BBV22 Location Isolater alignment work
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 13:08 | 14:55 | 1:47 | Breakdown Maintenance | 3001 | Brake chain - fuse opened. | Reboot and start the wtg
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 1:52 | 1:56 | 0:04 | Breakdown Maintenance | 10037 | All sensors of generator bearing temperature NDE defective (Short cut or wire break). | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 15:24 | 15:32 | 0:08 | Breakdown Maintenance | 1024 | Wind direction difference error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV17 | 3 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 0:06 | 0:10 | 0:04 | Breakdown Maintenance | 1023 | Wind speed difference error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 4:40 | 5:00 | 0:20 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 18:13 | 18:17 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV17 | 3 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 10:43 | 10:51 | 0:08 | Breakdown Maintenance | 11020 | Grid frequency from converter below operation range. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 18:12 | 19:05 | 0:53 | Internal Shutdown | IG01 | Internal shutdown | Feeder LC taken for BBV 23 Jumper work
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 22:00 | 22:04 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 19:51 | 19:59 | 0:08 | Breakdown Maintenance | 1024 | Wind direction difference error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 20:03 | 20:07 | 0:04 | Breakdown Maintenance | 2025 | Blade 2: Too big deviations from model (inside hysteresis). | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 21:11 | 23:59 | 2:48 | Breakdown Maintenance | 30015 | Fuse of yaw motor brake is open. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 0:30 | 13:08 | 12:38 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Checked all related connections ,Precharge fuse & conatctor replaced and wtg restored
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 2:12 | 2:20 | 0:08 | Breakdown Maintenance | 30015 | Fuse of yaw motor brake is open. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 16:46 | 19:44 | 2:58 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 20:37 | 20:45 | 0:08 | Breakdown Maintenance | 1024 | Wind direction difference error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 22:18 | 22:22 | 0:04 | Breakdown Maintenance | 30015 | Fuse of yaw motor brake is open. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 7:26 | 7:30 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 17:05 | 17:17 | 0:12 | Breakdown Maintenance | 1023 | Wind speed difference error. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 19:37 | 19:49 | 0:12 | Breakdown Maintenance | 30015 | Fuse of yaw motor brake is open. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 21:52 | 21:56 | 0:04 | Breakdown Maintenance | 30015 | Fuse of yaw motor brake is open. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 7:39 | 8:05 | 0:26 | Breakdown Maintenance | 30015 | Fuse of yaw motor brake is open. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 8:41 | 8:45 | 0:04 | Breakdown Maintenance | 1023 | Wind speed difference error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 11:16 | 14:12 | 2:56 | Internal Shutdown | IG03 | Over Current | Feeder LC taken for New wtg BBV20 line jumpering work
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 17:30 | 18:15 | 0:45 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV17 | 3 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV17 | 3 | FORCE MAJEURE | 19:52 | 20:00 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV17 | 3 | FORCE MAJEURE | 2:45 | 11:30 | 8:45 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV17 | 3 | FORCE MAJEURE | 14:28 | 14:32 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV17 | 3 | FORCE MAJEURE | 13:37 | 13:41 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV17 | 3 | FORCE MAJEURE | 14:36 | 14:40 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV17 | 3 | FORCE MAJEURE | 10:18 | 10:22 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV17 | 3 | FORCE MAJEURE | 22:40 | 22:44 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV17 | 3 | FORCE MAJEURE | 3:04 | 3:08 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV17 | 3 | FORCE MAJEURE | 16:22 | 16:26 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 18:59 | 19:05 | 0:06 | Internal Shutdown | IG01 | Internal shutdown | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 6:41 | 6:45 | 0:04 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 11:28 | 11:48 | 0:20 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 11:29 | 11:36 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 12:44 | 12:52 | 0:08 | Feeder tripped E/F | 9010 | Gearbox main bearing temperature 2 above error limit. | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV17 | 3 | GA INT | 14:10 | 16:30 | 2:20 | Feeder tripped E/F | 4027 | Alarm that stator breaker control sequence state machine detected an error. | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 10:59 | 13:40 | 2:41 | Breakdown Maintenance | 30015 | Fuse of yaw motor brake is open. | Check and replaced 24V fuse and start wtg
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 11:00 | 12:39 | 1:39 | Breakdown Maintenance | 10033 | Generator bearing temperature DE above error limit. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-20 | Karnataka | Bagewadi | BBV17 | 3 | WTG | 12:53 | 13:21 | 0:28 | Breakdown Maintenance | 28013 | Generator cooling fan M2 overload switch is open/tripped. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 13:52 | 13:56 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 12:41 | 13:01 | 0:20 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 15:01 | 15:05 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 17:20 | 17:24 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 17:36 | 17:58 | 0:22 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 13:00 | 13:20 | 0:20 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 0:47 | 0:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 0:52 | 3:50 | 2:58 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | converter reboot reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-07 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 13:57 | 14:01 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 0:46 | 0:50 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 22:06 | 22:22 | 0:16 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 6:50 | 6:58 | 0:08 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 1:01 | 1:13 | 0:12 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 10:51 | 11:10 | 0:19 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 22:18 | 22:26 | 0:08 | Breakdown Maintenance | 1003 | Anemometer 1 communication error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV18 | 3 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 15:47 | 17:03 | 1:16 | Breakdown Maintenance | 21054 | SLC: Emergency stop module in error state. | Checked related connection reboot and start the wtg
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 12:45 | 13:08 | 0:23 | Internal Shutdown | IG01 | Internal shutdown | Feeder internal shut down for BBV22 Location Isolater alignment work
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 13:08 | 15:30 | 2:22 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | VCB charged then reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 0:44 | 0:52 | 0:08 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 4:21 | 4:29 | 0:08 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 14:39 | 14:47 | 0:08 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV18 | 3 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 15:46 | 15:50 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 11:09 | 11:17 | 0:08 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 14:54 | 14:58 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 18:28 | 18:40 | 0:12 | Breakdown Maintenance | 1003 | Anemometer 1 communication error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV18 | 3 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 18:12 | 19:05 | 0:53 | Internal Shutdown | IG01 | Internal shutdown | Feeder LC taken for BBV 23 Jumper work
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 19:05 | 23:59 | 4:54 | Breakdown Maintenance | 21070 | SLC: Yaw control device twist protection switch tripped. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-24 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 13:28 | 13:32 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 12:32 | 12:36 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 23:25 | 23:40 | 0:15 | Breakdown Maintenance | 1003 | Anemometer 1 communication error. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 5:14 | 5:18 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 2:09 | 2:13 | 0:04 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 14:14 | 14:22 | 0:08 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 16:46 | 19:44 | 2:58 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 21:10 | 21:18 | 0:08 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 4:40 | 6:20 | 1:40 | Breakdown Maintenance | 4020 | Stator breaker tripped. | ACB spring charge indication broken then corrected and reset start wtg
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 0:41 | 0:45 | 0:04 | Breakdown Maintenance | 26009 | Offset of the tower-vibration sensor in drivetrain direction above error limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 14:08 | 14:12 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 14:38 | 14:42 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 18:48 | 18:56 | 0:08 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 3:25 | 7:25 | 4:00 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | After replacement of Left1 Anemometer and its surge arrestor restored WTG.
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 10:06 | 10:10 | 0:04 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 11:16 | 14:12 | 2:56 | Internal Shutdown | IG03 | Over Current | Feeder LC taken for New wtg BBV20 line jumpering work
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 15:17 | 15:24 | 0:07 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 18:00 | 18:04 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 11:05 | 11:09 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 17:30 | 18:15 | 0:45 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV18 | 3 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 21:00 | 21:04 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 4:29 | 4:33 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 0:38 | 1:32 | 0:54 | Covid 19 | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 16:36 | 16:40 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 20:19 | 20:23 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 20:46 | 20:50 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 0:09 | 0:13 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 2:47 | 2:51 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 15:12 | 15:16 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 20:52 | 21:00 | 0:08 | Covid 19 |  |  | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV18 | 3 | FORCE MAJEURE | 21:05 | 21:09 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 18:59 | 19:05 | 0:06 | Internal Shutdown | IG01 | Internal shutdown | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 0:26 | 0:38 | 0:12 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 4:08 | 4:42 | 0:34 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 11:29 | 11:36 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 12:44 | 12:52 | 0:08 | Feeder tripped E/F | 9010 | Gearbox main bearing temperature 2 above error limit. | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV18 | 3 | GA INT | 14:10 | 16:30 | 2:20 | Feeder tripped E/F | 4027 | Alarm that stator breaker control sequence state machine detected an error. | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 13:54 | 13:58 | 0:04 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 14:29 | 14:33 | 0:04 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 15:55 | 16:03 | 0:08 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 22:20 | 22:24 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-20 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 6:46 | 6:53 | 0:07 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-20 | Karnataka | Bagewadi | BBV18 | 3 | WTG | 14:24 | 14:44 | 0:20 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 0:24 | 0:32 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 15:19 | 15:27 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 0:46 | 0:54 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 15:08 | 15:16 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 0:47 | 0:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 8:00 | 11:58 | 3:58 | Breakdown Maintenance | 4130 | CC101 24VDC power supply for actuators is in fault state. | CC101 panel 24V power supply replaced then reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-07 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 0:45 | 1:02 | 0:17 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 20:52 | 21:00 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 15:50 | 16:35 | 0:45 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 12:59 | 13:15 | 0:16 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV21 | 3 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 12:45 | 13:08 | 0:23 | Internal Shutdown | IG01 | Internal shutdown | Feeder internal shut down for BBV22 Location Isolater alignment work
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 13:08 | 14:55 | 1:47 | Breakdown Maintenance | 3001 | Brake chain - fuse opened. | Reboot and start the wtg
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 14:07 | 14:12 | 0:05 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV21 | 3 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 0:38 | 1:02 | 0:24 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 17:37 | 18:00 | 0:23 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 5:52 | 6:16 | 0:24 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 13:52 | 14:14 | 0:22 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV21 | 3 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 18:12 | 19:05 | 0:53 | Internal Shutdown | IG01 | Internal shutdown | Feeder LC taken for BBV 23 Jumper work
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 19:05 | 23:59 | 4:54 | Breakdown Maintenance | 21054 | SLC: Emergency stop module in error state. | VCB charged then reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 18:26 | 18:30 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 22:18 | 23:37 | 1:19 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Reboot and start the wtg
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 22:41 | 22:45 | 0:04 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 1:03 | 1:07 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 16:46 | 19:44 | 2:58 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 21:29 | 21:33 | 0:04 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 19:03 | 19:11 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 21:24 | 21:32 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV21 | 3 | FORCE MAJEURE | 11:14 | 24:00 | 12:46 | Covid 19 | 14004 | Hydraulic unit oil level is too low. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV21 | 3 | FORCE MAJEURE | 0:00 | 13:53 | 13:53 | Covid 19 | 14004 | Hydraulic unit oil level is too low. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 19:33 | 19:41 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 11:16 | 14:12 | 2:56 | Internal Shutdown | IG03 | Over Current | Feeder LC taken for New wtg BBV20 line jumpering work
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV21 | 3 | FORCE MAJEURE | 18:03 | 18:11 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV21 | 3 | FORCE MAJEURE | 20:14 | 20:18 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV21 | 3 | FORCE MAJEURE | 12:22 | 12:30 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 17:30 | 18:15 | 0:45 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV21 | 3 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV21 | 3 | FORCE MAJEURE | 18:29 | 18:37 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV21 | 3 | FORCE MAJEURE | 10:54 | 10:58 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV21 | 3 | FORCE MAJEURE | 15:40 | 15:48 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV21 | 3 | FORCE MAJEURE | 11:13 | 11:21 | 0:08 | Covid 19 |  |  | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 18:59 | 19:05 | 0:06 | Internal Shutdown | IG01 | Internal shutdown | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 0:05 | 0:46 | 0:41 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 11:29 | 11:36 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 12:44 | 12:52 | 0:08 | Feeder tripped E/F | 9010 | Gearbox main bearing temperature 2 above error limit. | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV21 | 3 | GA INT | 14:10 | 16:30 | 2:20 | Feeder tripped E/F | 4027 | Alarm that stator breaker control sequence state machine detected an error. | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 0:21 | 1:15 | 0:54 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 1:13 | 1:45 | 0:32 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 9:49 | 10:20 | 0:31 | Breakdown Maintenance | 30006 | Nacelle rotation overspeed. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 16:37 | 16:41 | 0:04 | Breakdown Maintenance | 4031 | External diode temperature above error limit. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV21 | 3 | WTG | 7:53 | 8:03 | 0:10 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 18:11 | 18:15 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 17:08 | 17:36 | 0:28 | Breakdown Maintenance | 21009 | Safety chain - Overspeed detected by overspeed relay. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 0:47 | 0:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 0:52 | 2:00 | 1:08 | Breakdown Maintenance | 11020 | Grid frequency from converter below operation range. | converter reboot reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV25 | 3 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 7:20 | 9:30 | 2:10 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Checked and Converter parameter updated and wtg restored
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 12:45 | 13:08 | 0:23 | Internal Shutdown | IG01 | Internal shutdown | Feeder internal shut down for BBV22 Location Isolater alignment work
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 13:08 | 14:30 | 1:22 | Breakdown Maintenance | 11020 | Grid frequency from converter below operation range. | converter parameter updated and wtg started
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 13:49 | 13:57 | 0:08 | Breakdown Maintenance | 11015 | Fuse for power measurement device voltage measurement is open/broken. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 14:47 | 14:51 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV25 | 3 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 16:37 | 16:41 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV25 | 3 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 7:05 | 8:40 | 1:35 | Breakdown Maintenance | 7528 | Converter error detected. For details see additional alarms. | converter reboot reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 18:12 | 19:05 | 0:53 | Internal Shutdown | IG01 | Internal shutdown | Feeder LC taken for BBV 23 Jumper work
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 19:05 | 21:00 | 1:55 | Breakdown Maintenance | 11020 | Grid frequency from converter below operation range. | converter reboot reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-24 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 13:08 | 13:24 | 0:16 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 7:30 | 7:34 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 22:15 | 22:19 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 12:27 | 12:50 | 0:23 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 15:12 | 15:21 | 0:09 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 16:46 | 19:44 | 2:58 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 19:44 | 21:22 | 1:38 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Safety chain closed then reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 14:28 | 14:32 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 11:00 | 11:08 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 14:45 | 14:53 | 0:08 | Breakdown Maintenance | 47018 | Analog environment temperature below error limit. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 17:18 | 17:22 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 15:49 | 15:57 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 11:16 | 14:12 | 2:56 | Internal Shutdown | IG03 | Over Current | Feeder LC taken for New wtg BBV20 line jumpering work
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 16:11 | 16:15 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 16:18 | 16:25 | 0:07 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 17:30 | 18:15 | 0:45 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV25 | 3 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 18:58 | 21:30 | 2:32 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 11:15 | 11:23 | 0:08 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 18:06 | 24:00 | 5:54 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 0:00 | 12:10 | 12:10 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 11:12 | 11:16 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 13:59 | 14:46 | 0:47 | Covid 19 |  |  | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 11:53 | 12:01 | 0:08 | Covid 19 |  |  | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV25 | 3 | FORCE MAJEURE | 13:44 | 14:05 | 0:21 | Covid 19 |  |  | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 10:35 | 10:39 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 18:59 | 19:05 | 0:06 | Internal Shutdown | IG01 | Internal shutdown | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 19:05 | 22:19 | 3:14 | Breakdown Maintenance | 11020 | Grid frequency from converter below operation range. | converter reboot reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 11:29 | 11:36 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV25 | 3 | WTG | 11:36 | 13:20 | 1:44 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | converter reboot reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 12:44 | 12:52 | 0:08 | Feeder tripped E/F | 9010 | Gearbox main bearing temperature 2 above error limit. | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV25 | 3 | GA INT | 14:10 | 16:30 | 2:20 | Feeder tripped E/F | 4027 | Alarm that stator breaker control sequence state machine detected an error. | over current earth fault
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 16:05 | 16:09 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 17:16 | 17:49 | 0:33 | Breakdown Maintenance | 21064 | Emergency Button TB100 pressed | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 18:20 | 19:32 | 1:12 | Breakdown Maintenance | 12004 | Monitoring of hub grid contactor. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV39 | 4 | GA INT | 9:40 | 10:58 | 1:18 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for project BBV47 new line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 16:58 | 17:02 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV39 | 4 | GA INT | 14:53 | 16:50 | 1:57 | Internal Shutdown | IG04 | Internal shutdown by project | Feeder Internal shut down for project new line jumper work
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 19:31 | 19:35 | 0:04 | Breakdown Maintenance | 10044 | Generator grounding brush worn error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 19:46 | 19:50 | 0:04 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 19:54 | 19:58 | 0:04 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-07 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 14:54 | 15:30 | 0:36 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 18:10 | 18:35 | 0:25 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 4:42 | 6:15 | 1:33 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Check & found DC 24V fuse failure , replaced with new fuse and wtg restored
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 11:48 | 12:20 | 0:32 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 6:22 | 6:26 | 0:04 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | auto reset
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV39 | 4 | GA INT | 14:08 | 17:48 | 3:40 | Internal Shutdown | IG04 | Internal shutdown by project | Internal shutdown for project NEW line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV39 | 4 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 12:27 | 12:31 | 0:04 | Breakdown Maintenance | 24001 | Drive train swinging. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 1:24 | 2:31 | 1:07 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 8:54 | 10:18 | 1:24 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 10:22 | 10:26 | 0:04 | Breakdown Maintenance | 9035 | Gearbox oil filter 100% clogged. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 5:54 | 6:38 | 0:44 | Breakdown Maintenance | 21064 | Emergency Button TB100 pressed | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 11:35 | 12:15 | 0:40 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV39 | 4 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 20:42 | 20:46 | 0:04 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 0:17 | 1:03 | 0:46 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 0:34 | 0:38 | 0:04 | Breakdown Maintenance | 12080 | Blade 2: Error at referencing. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 7:52 | 8:04 | 0:12 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV39 | 4 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 17:29 | 17:37 | 0:08 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 10:43 | 10:47 | 0:04 | Breakdown Maintenance | 24001 | Drive train swinging. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 14:47 | 14:55 | 0:08 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 8:01 | 8:21 | 0:20 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 17:36 | 17:40 | 0:04 | Breakdown Maintenance | 47014 | Analog environment temperature sensors defective. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-24 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 11:37 | 11:49 | 0:12 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-24 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 14:18 | 14:22 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 2:59 | 3:03 | 0:04 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 15:07 | 15:11 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 15:43 | 15:47 | 0:04 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 10:44 | 10:56 | 0:12 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV39 | 4 | GA INT | 16:52 | 16:59 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 21:45 | 23:10 | 1:25 | Breakdown Maintenance | 47018 | Analog environment temperature below error limit. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 22:15 | 22:19 | 0:04 | Breakdown Maintenance | 21064 | Emergency Button TB100 pressed | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 15:22 | 15:30 | 0:08 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 17:28 | 18:31 | 1:03 | Breakdown Maintenance |  |  | MS for HT yard isolator aliments work
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 13:46 | 14:02 | 0:16 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 2:56 | 3:04 | 0:08 | Breakdown Maintenance | 21064 | Emergency Button TB100 pressed | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 5:43 | 6:07 | 0:24 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 9:57 | 10:17 | 0:20 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 19:27 | 19:31 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 10:32 | 10:36 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV39 | 4 | GA INT | 17:57 | 18:15 | 0:18 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV39 | 4 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 11:37 | 11:53 | 0:16 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 13:45 | 13:49 | 0:04 | Covid 19 | 7628 | The detected grid state from converter is faulted or not OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 14:28 | 14:40 | 0:12 | Covid 19 | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 0:04 | 0:22 | 0:18 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 16:50 | 16:54 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 0:49 | 1:05 | 0:16 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 12:30 | 12:34 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 18:06 | 18:10 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 11:43 | 11:59 | 0:16 | Covid 19 |  |  | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 0:50 | 0:54 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 12:43 | 12:47 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV39 | 4 | FORCE MAJEURE | 5:10 | 15:55 | 10:45 | Covid 19 | 23007 | Converter healthcheck alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 17:02 | 17:11 | 0:09 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 0:52 | 1:05 | 0:13 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 14:54 | 15:02 | 0:08 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 9:52 | 10:22 | 0:30 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 12:07 | 12:15 | 0:08 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 13:33 | 13:37 | 0:04 | Breakdown Maintenance | 10044 | Generator grounding brush worn error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 13:56 | 14:18 | 0:22 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV39 | 4 | WTG | 17:43 | 18:05 | 0:22 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 0:00 | 1:50 | 1:50 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Work is completed
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 21:55 | 21:59 | 0:04 | Breakdown Maintenance | 7614 | Converter system fault is active. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 4:57 | 5:05 | 0:08 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 10:53 | 10:57 | 0:04 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 7:13 | 7:26 | 0:13 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV40 | 4 | GA INT | 9:40 | 10:58 | 1:18 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for project BBV47 new line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 12:20 | 12:28 | 0:08 | Breakdown Maintenance | 1018 | Anemometer 2 low wind speed error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV40 | 4 | GA INT | 14:53 | 16:50 | 1:57 | Internal Shutdown | IG04 | Internal shutdown by project | Feeder Internal shut down for project new line jumper work
Giriraj Enterprises - Bagewadi | 2021-04-07 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 6:26 | 6:30 | 0:04 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-07 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 18:18 | 18:22 | 0:04 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 0:47 | 1:35 | 0:48 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 8:03 | 8:07 | 0:04 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 8:11 | 10:21 | 2:10 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 0:08 | 0:12 | 0:04 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 9:12 | 9:16 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV40 | 4 | GA INT | 14:08 | 17:48 | 3:40 | Internal Shutdown | IG04 | Internal shutdown by project | Internal shutdown for project NEW line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 2:12 | 2:24 | 0:12 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 11:16 | 11:24 | 0:08 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-11 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 20:45 | 20:49 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | auto reset
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV40 | 4 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 17:56 | 18:00 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | auto reset
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 12:01 | 12:21 | 0:20 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 22:18 | 22:51 | 0:33 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 0:50 | 1:20 | 0:30 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 7:16 | 7:20 | 0:04 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 9:19 | 10:15 | 0:56 | Breakdown Maintenance | 1018 | Anemometer 2 low wind speed error. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 12:37 | 12:41 | 0:04 | Breakdown Maintenance | 26015 | Tower vibration (acceleration peak-to-peak value) in drivetrain direction delayed is above limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 16:37 | 16:41 | 0:04 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 6:12 | 6:16 | 0:04 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 7:55 | 8:03 | 0:08 | Breakdown Maintenance | 26009 | Offset of the tower-vibration sensor in drivetrain direction above error limit | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 9:46 | 9:54 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV40 | 4 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 18:23 | 18:31 | 0:08 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 5:12 | 5:20 | 0:08 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 10:51 | 10:55 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | auto reset
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 12:42 | 12:46 | 0:04 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV40 | 4 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 7:41 | 7:49 | 0:08 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 8:51 | 8:55 | 0:04 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 9:27 | 9:31 | 0:04 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 10:36 | 10:40 | 0:04 | Breakdown Maintenance | 24001 | Drive train swinging. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 11:59 | 12:03 | 0:04 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 18:31 | 18:47 | 0:16 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 2:27 | 2:31 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 2:58 | 3:24 | 0:26 | Breakdown Maintenance | 23011 | Brake healthcheck alarm. | Reboot and start the wtg
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 12:29 | 12:33 | 0:04 | Breakdown Maintenance | 23011 | Brake healthcheck alarm. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-26 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 18:35 | 18:39 | 0:04 | Breakdown Maintenance | 23011 | Brake healthcheck alarm. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 5:50 | 5:58 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 4:51 | 4:55 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 7:40 | 7:44 | 0:04 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV40 | 4 | GA INT | 16:52 | 16:59 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 2:40 | 2:44 | 0:04 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 16:22 | 16:26 | 0:04 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 0:57 | 1:01 | 0:04 | Breakdown Maintenance | 1014 | Anemometer 2 communication error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 14:30 | 14:34 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 4:58 | 5:02 | 0:04 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 8:14 | 8:21 | 0:07 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 17:28 | 19:12 | 1:44 | Breakdown Maintenance |  |  | MS for HT yard isolator aliments work
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 17:10 | 21:42 | 4:32 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Stator breaker replacement work done and reset then start wtg
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 2:44 | 2:48 | 0:04 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-04 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 21:46 | 21:50 | 0:04 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-05 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 12:28 | 12:32 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 14:54 | 14:58 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV40 | 4 | GA INT | 17:57 | 18:15 | 0:18 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV40 | 4 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 15:20 | 15:24 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 19:59 | 20:03 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 1:05 | 1:09 | 0:04 | Covid 19 | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 18:01 | 18:05 | 0:04 | Covid 19 | 26015 | Tower vibration (acceleration peak-to-peak value) in drivetrain direction delayed is above limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 16:42 | 16:46 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 20:05 | 20:17 | 0:12 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 17:39 | 17:43 | 0:04 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 15:20 | 15:24 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 22:04 | 22:08 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV40 | 4 | FORCE MAJEURE | 21:54 | 21:58 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-14 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 12:49 | 12:53 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 11:29 | 11:33 | 0:04 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 7:03 | 7:24 | 0:21 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 11:05 | 11:17 | 0:12 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-17 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 10:30 | 14:10 | 3:40 | Breakdown Maintenance | 12026 | Hub grid fuse has opened. | Checked all hub cabinets found all heating cables ok thenstart wtg
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 20:12 | 20:16 | 0:04 | Breakdown Maintenance | 10044 | Generator grounding brush worn error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 23:37 | 23:42 | 0:05 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 0:12 | 1:20 | 1:08 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-20 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 17:56 | 18:00 | 0:04 | Breakdown Maintenance | 7782 | Generator underspeed fault. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-20 | Karnataka | Bagewadi | BBV40 | 4 | WTG | 19:17 | 19:21 | 0:04 | Breakdown Maintenance | 26015 | Tower vibration (acceleration peak-to-peak value) in drivetrain direction delayed is above limit | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 1:34 | 1:38 | 0:04 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 16:58 | 17:02 | 0:04 | Breakdown Maintenance | 12105 | Blade 3: IPS was active in wrong area. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 1:45 | 18:35 | 16:50 | Breakdown Maintenance | 12008 | Non plausible pitch state difference. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 9:46 | 9:54 | 0:08 | Breakdown Maintenance | 12073 | Blade 2: IPS was active in wrong area. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV42 | 4 | GA INT | 9:40 | 10:58 | 1:18 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for project BBV47 new line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 20:05 | 24:00 | 3:55 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Work in process.
Giriraj Enterprises - Bagewadi | 2021-04-05 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 0:00 | 1:20 | 1:20 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Check and found 550 Amp fuse & busbar faulty then replaced and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV42 | 4 | GA INT | 14:53 | 16:50 | 1:57 | Internal Shutdown | IG04 | Internal shutdown by project | Feeder Internal shut down for project new line jumper work
Giriraj Enterprises - Bagewadi | 2021-04-08 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 19:11 | 19:18 | 0:07 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV42 | 4 | GA INT | 14:08 | 17:48 | 3:40 | Internal Shutdown | IG04 | Internal shutdown by project | Internal shutdown for project NEW line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV42 | 4 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 1:04 | 1:26 | 0:22 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 8:05 | 8:09 | 0:04 | Breakdown Maintenance | 10029 | All sensors of generator bearing temperature DE defective (Short cut or wire break). | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 10:33 | 10:37 | 0:04 | Breakdown Maintenance | 10029 | All sensors of generator bearing temperature DE defective (Short cut or wire break). | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-16 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 1:24 | 2:12 | 0:48 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV42 | 4 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 11:33 | 13:02 | 1:29 | Breakdown Maintenance |  |  | Ms for repetative error work
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 16:35 | 17:00 | 0:25 | Breakdown Maintenance |  |  | Ms for repetative error work
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 3:05 | 11:42 | 8:37 | Breakdown Maintenance | 7546 | Line side breaker is closed when commanded to be open. | Check and found line contactor auxiliray feedaback switch failure replaced and wtg start
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV42 | 4 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 5:40 | 5:44 | 0:04 | Breakdown Maintenance | 10029 | All sensors of generator bearing temperature DE defective (Short cut or wire break). | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV42 | 4 | GA INT | 16:52 | 16:59 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 15:04 | 15:08 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV42 | 4 | GA INT | 17:57 | 18:15 | 0:18 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV42 | 4 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV42 | 4 | FORCE MAJEURE | 19:51 | 19:59 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-07 | Karnataka | Bagewadi | BBV42 | 4 | FORCE MAJEURE | 20:08 | 24:00 | 3:52 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV42 | 4 | FORCE MAJEURE | 0:00 | 9:20 | 9:20 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reboot then reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV42 | 4 | FORCE MAJEURE | 17:25 | 24:00 | 6:35 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-10 | Karnataka | Bagewadi | BBV42 | 4 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-11 | Karnataka | Bagewadi | BBV42 | 4 | FORCE MAJEURE | 0:00 | 16:30 | 16:30 | Covid 19 |  |  | Replaced rotor encoder cable & CNT module then reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 11:19 | 11:31 | 0:12 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV42 | 4 | WTG | 16:15 | 16:19 | 0:04 | Breakdown Maintenance | 1007 | Anemometer 1 low wind error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 11:51 | 11:55 | 0:04 | Breakdown Maintenance | 12122 | Blade 3: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-02 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 15:03 | 15:07 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV43 | 4 | GA INT | 9:40 | 10:58 | 1:18 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for project BBV47 new line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 10:58 | 11:50 | 0:52 | Breakdown Maintenance | 3001 | Brake chain - fuse opened. | Close Brake chain reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV43 | 4 | GA INT | 14:53 | 16:50 | 1:57 | Internal Shutdown | IG04 | Internal shutdown by project | Feeder Internal shut down for project new line jumper work
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 16:50 | 17:50 | 1:00 | Breakdown Maintenance | 3001 | Brake chain - fuse opened. | Close Brake chain reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 12:06 | 12:14 | 0:08 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV43 | 4 | GA INT | 14:08 | 17:48 | 3:40 | Internal Shutdown | IG04 | Internal shutdown by project | Internal shutdown for project NEW line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 17:52 | 19:45 | 1:53 | Breakdown Maintenance | 3001 | Brake chain - fuse opened. | Converter parameter updated and wtg restored
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV43 | 4 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 12:40 | 14:42 | 2:02 | Breakdown Maintenance | 12122 | Blade 3: IPS not active in blade state STOP_OK. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV43 | 4 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 18:09 | 18:13 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 3:57 | 4:05 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 14:32 | 14:40 | 0:08 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-19 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 15:32 | 15:40 | 0:08 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 15:08 | 15:12 | 0:04 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV43 | 4 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 10:47 | 10:55 | 0:08 | Breakdown Maintenance | 11015 | Fuse for power measurement device voltage measurement is open/broken. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 14:37 | 14:41 | 0:04 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 13:14 | 13:18 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 20:10 | 20:14 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-24 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 11:30 | 11:34 | 0:04 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-25 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 14:41 | 14:49 | 0:08 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 16:54 | 16:58 | 0:04 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV43 | 4 | GA INT | 16:52 | 16:59 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 18:30 | 20:05 | 1:35 | Breakdown Maintenance | 3001 | Brake chain - fuse opened. | Brake chain closed then reset and start wtg
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 7:48 | 7:56 | 0:08 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 11:38 | 11:42 | 0:04 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 20:02 | 20:06 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 15:06 | 15:10 | 0:04 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 10:44 | 10:48 | 0:04 | Breakdown Maintenance | 12122 | Blade 3: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 17:03 | 17:07 | 0:04 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV43 | 4 | GA INT | 17:57 | 18:15 | 0:18 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV43 | 4 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-08 | Karnataka | Bagewadi | BBV43 | 4 | FORCE MAJEURE | 10:28 | 10:36 | 0:08 | Covid 19 | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV43 | 4 | FORCE MAJEURE | 10:39 | 10:47 | 0:08 | Covid 19 |  |  | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-15 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 11:15 | 11:27 | 0:12 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV43 | 4 | WTG | 4:10 | 4:18 | 0:08 | Breakdown Maintenance | 12122 | Blade 3: IPS not active in blade state STOP_OK. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-01 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 22:46 | 22:50 | 0:04 | Breakdown Maintenance | 7050 | Converter LSA: Pole 1 IGBT desaturation fault | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-03 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 17:03 | 17:26 | 0:23 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV46 | 4 | GA INT | 9:40 | 10:58 | 1:18 | Internal Shutdown | IG01 | Internal shutdown | Mannuly stopped for project BBV47 new line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-04 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 11:21 | 11:29 | 0:08 | Breakdown Maintenance | 23006 | Converter healthcheck timeout. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-06 | Karnataka | Bagewadi | BBV46 | 4 | GA INT | 14:53 | 16:50 | 1:57 | Internal Shutdown | IG04 | Internal shutdown by project | Feeder Internal shut down for project new line jumper work
Giriraj Enterprises - Bagewadi | 2021-04-09 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 17:44 | 17:52 | 0:08 | Breakdown Maintenance | 7050 | Converter LSA: Pole 1 IGBT desaturation fault | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-10 | Karnataka | Bagewadi | BBV46 | 4 | GA INT | 14:08 | 17:48 | 3:40 | Internal Shutdown | IG04 | Internal shutdown by project | Internal shutdown for project NEW line jumper connection work
Giriraj Enterprises - Bagewadi | 2021-04-12 | Karnataka | Bagewadi | BBV46 | 4 | GA EXT | 5:54 | 7:14 | 1:20 | External Breakdown | EG02 | Grid Breakdown | 220Kv grid failure
Giriraj Enterprises - Bagewadi | 2021-04-13 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 19:46 | 19:50 | 0:04 | Breakdown Maintenance | 7050 | Converter LSA: Pole 1 IGBT desaturation fault | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-14 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 9:23 | 9:31 | 0:08 | Breakdown Maintenance | 7050 | Converter LSA: Pole 1 IGBT desaturation fault | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-15 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 8:22 | 9:53 | 1:31 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Checked related connections and fuse replaced and wtg restored
Giriraj Enterprises - Bagewadi | 2021-04-17 | Karnataka | Bagewadi | BBV46 | 4 | GA EXT | 16:34 | 17:04 | 0:30 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-18 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 3:57 | 4:01 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-20 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 17:54 | 18:10 | 0:16 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-21 | Karnataka | Bagewadi | BBV46 | 4 | GA EXT | 6:50 | 7:05 | 0:15 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 10:07 | 10:15 | 0:08 | Breakdown Maintenance | 11015 | Fuse for power measurement device voltage measurement is open/broken. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-22 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 20:58 | 21:02 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-23 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 14:59 | 15:03 | 0:04 | Breakdown Maintenance | 7137 | Converter GSA: Low line fault | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-24 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 16:41 | 16:53 | 0:12 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-27 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 16:50 | 16:58 | 0:08 | Breakdown Maintenance | 31021 | Blade teeth lubrication is in maintenance state. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-04-28 | Karnataka | Bagewadi | BBV46 | 4 | GA INT | 16:52 | 16:59 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-04-29 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 18:13 | 19:49 | 1:36 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Reboot and reset Start wtg
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 6:20 | 6:24 | 0:04 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-04-30 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 14:31 | 14:39 | 0:08 | Breakdown Maintenance | 12048 | Blade 1: Error at referencing. | Reset and start
Giriraj Enterprises - Bagewadi | 2021-05-01 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 15:06 | 15:10 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-02 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 20:38 | 21:02 | 0:24 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-03 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 17:07 | 18:10 | 1:03 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV46 | 4 | GA INT | 17:57 | 18:15 | 0:18 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to earth fault
Giriraj Enterprises - Bagewadi | 2021-05-06 | Karnataka | Bagewadi | BBV46 | 4 | GA EXT | 18:15 | 18:58 | 0:43 | External Breakdown | EG02 | Grid Breakdown | 220Kv main supply failure
Giriraj Enterprises - Bagewadi | 2021-05-09 | Karnataka | Bagewadi | BBV46 | 4 | FORCE MAJEURE | 19:29 | 19:37 | 0:08 | Covid 19 |  |  | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises - Bagewadi | 2021-05-12 | Karnataka | Bagewadi | BBV46 | 4 | FORCE MAJEURE | 22:51 | 22:55 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-13 | Karnataka | Bagewadi | BBV46 | 4 | FORCE MAJEURE | 18:32 | 18:36 | 0:04 | Covid 19 |  |  | Auto reset
Giriraj Enterprises - Bagewadi | 2021-05-16 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 9:58 | 10:46 | 0:48 | Breakdown Maintenance | 7050 | Converter LSA: Pole 1 IGBT desaturation fault | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-18 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 14:53 | 15:25 | 0:32 | Breakdown Maintenance | 7786 |  | Reboot and reset
Giriraj Enterprises - Bagewadi | 2021-05-19 | Karnataka | Bagewadi | BBV46 | 4 | WTG | 18:44 | 18:52 | 0:08 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reset and start
Giriraj Enterprises | 2021-04-01 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Require material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Require material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-03 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Require material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-04 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Require material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 9:30 | 9:30 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Require material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 9:30 | 16:30 | 7:00 | Preventive Maintenance |  |  | WTG yearly preventive maintenance work done.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 16:30 | 24:00 | 7:30 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Require material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Require material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Required material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-08 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Required material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 3:34 | 3:34 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Required material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT11 | 1 | GA INT | 3:34 | 3:48 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 3:48 | 24:00 | 20:12 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Generator cooling radiator replaced , required material GB oil hose and coolant to restored WTG.
Giriraj Enterprises | 2021-04-10 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Required material generator cooling radiator to restored WTG.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Required material GCU coolant and GB oil hose to restored WTG.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Required material GCU coolant and GB oil hose to restored WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 0:00 | 13:40 | 13:40 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Fillup colant in GCU & Replace GB hose pipe then start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT11 | 1 | GA EXT | 17:32 | 18:38 | 1:06 | External Breakdown | EG02 | Grid Breakdown | GSS transformer Tripped checked and charged from substation.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 18:38 | 18:42 | 0:04 | Breakdown Maintenance | 7136 | Converter GSA: High line fault | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT11 | 1 | GA EXT | 22:16 | 22:26 | 0:10 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken for load changing purpose by EB.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 22:26 | 22:30 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT11 | 1 | GA INT | 9:38 | 16:21 | 6:43 | Internal shutdown | IG01 | Internal shutdown | Internal line shoutdown taken for line maintence from site to nerele village.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 16:21 | 16:33 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT11 | 1 | GA INT | 7:43 | 11:43 | 4:00 | Internal shutdown | IG01 | Internal shutdown | Internal line shutdown taken for line maintenance from site to Phuphere Isolator.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 11:43 | 11:54 | 0:11 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT11 | 1 | GA EXT | 9:11 | 17:17 | 8:06 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken by EB for GSS pre mansoon maintenance work.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 17:17 | 17:29 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Bhendewade | BHT11 | 1 | GA INT | 1:02 | 1:16 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 1:16 | 1:20 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Bhendewade | BHT11 | 1 | FORCE MAJEURE | 11:51 | 24:00 | 12:09 | Covid 19 | 28006 | Generator cooling water pressure low alarm. | O & M team infected due to Covid-19 Pandemic, so WIP
Giriraj Enterprises | 2021-04-28 | Maharashtra | Bhendewade | BHT11 | 1 | FORCE MAJEURE | 0:00 | 10:30 | 10:30 | Covid 19 | 28006 | Generator cooling water pressure low alarm. | O & M team infected due to Covid-19 Pandemic, fillup coolant in GCU and checked any leakage not found and start WTG.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT11 | 1 | GA INT | 17:30 | 17:51 | 0:21 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 17:51 | 17:55 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG autorestarted after feeder charged.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT11 | 1 | BOC | 18:06 | 18:10 | 0:04 | Voltage difference | 7009 | Converter LSA: Low line fault | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT11 | 1 | BOC | 18:19 | 18:23 | 0:04 | Voltage difference | 2025 | Blade 2: Too big deviations from model (inside hysteresis). | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT11 | 1 | BOC | 18:38 | 18:42 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT11 | 1 | BOC | 23:03 | 23:07 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT11 | 1 | GA INT | 11:57 | 13:00 | 1:03 | Internal Shutdown | IG01 | Internal shutdown | Feeeder 1 shutdown taken on emergency basis for fault rectification of feeder 2.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 13:00 | 13:04 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charged WTG auto restarted.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT11 | 1 | BOC | 19:15 | 19:19 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | WTG auto reseted due to grid voltage fluctuation.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT11 | 1 | GA INT | 8:12 | 8:22 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked and feeder charged.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 8:22 | 8:26 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | WTG auto reseted after feeder no 1 charge.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT11 | 1 | WTG | 11:45 | 11:51 | 0:06 | Special Activity |  |  | Visually blade inspection done by binacular, then start WTG.
Giriraj Enterprises | 2021-04-03 | Maharashtra | Bhendewade | BHT14 | 1 | BOC | 5:37 | 5:41 | 0:04 | Voltage difference | 7391 | Converter GSA: Inverter System Fault | Error comes due to grid voltage fluctuation, WTG auto restarted.
Giriraj Enterprises | 2021-04-03 | Maharashtra | Bhendewade | BHT14 | 1 | BOC | 10:55 | 10:56 | 0:01 | Voltage difference | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Error comes due to grid voltage fluctuation, WTG auto restarted.
Giriraj Enterprises | 2021-04-04 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 22:53 | 22:57 | 0:04 | Breakdown Maintenance | 7140 | Converter GSA: Power Supply Fault 24V | WTG auto restarted.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT14 | 1 | BOC | 9:36 | 9:40 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Error comes due to grid voltage fluctuation, WTG autorestarted
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 11:57 | 12:25 | 0:28 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Check and reboot PLC then start WTG
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 15:07 | 15:20 | 0:13 | Special Activity | SA14 | Special Activity - WTG Critical Points Checking | Topup coolent in CCU and bottom 5S work done
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT14 | 1 | GA INT | 3:34 | 3:48 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 3:48 | 3:52 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | After feeder charged WTG auto reset.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT14 | 1 | GA EXT | 17:32 | 18:38 | 1:06 | External Breakdown | EG02 | Grid Breakdown | GSS transformer Tripped checked and charged from substation.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 18:38 | 18:42 | 0:04 | Breakdown Maintenance | 7136 | Converter GSA: High line fault | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT14 | 1 | GA EXT | 22:16 | 22:26 | 0:10 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken for load changing purpose by EB.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 22:26 | 22:30 | 0:04 | Breakdown Maintenance | 7009 | Converter LSA: Low line fault | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT14 | 1 | GA INT | 9:38 | 16:21 | 6:43 | Internal shutdown | IG01 | Internal shutdown | Internal line shoutdown taken for line maintence from site to nerele village.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 16:21 | 16:32 | 0:11 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT14 | 1 | GA INT | 7:43 | 11:43 | 4:00 | Internal shutdown | IG01 | Internal shutdown | Internal line shutdown taken for line maintenance from site to Phuphere Isolator.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 11:43 | 11:54 | 0:11 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT14 | 1 | GA EXT | 9:11 | 17:17 | 8:06 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken by EB for GSS pre mansoon maintenance work.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 17:17 | 17:38 | 0:21 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Bhendewade | BHT14 | 1 | GA INT | 1:02 | 1:16 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 1:16 | 1:20 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Bhendewade | BHT14 | 1 | FORCE MAJEURE | 16:37 | 16:57 | 0:20 | Covid 19 | 31019 | Blade teeth lubrication cyclic contactor not working when pump is on. | O & M team infected due to Covid-19 Pandemic, WTG manually restarted.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT14 | 1 | GA INT | 17:30 | 17:51 | 0:21 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 17:51 | 17:55 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG autorestarted after feeder charged.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT14 | 1 | BOC | 18:05 | 18:09 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT14 | 1 | BOC | 18:18 | 18:22 | 0:04 | Voltage difference | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT14 | 1 | BOC | 18:37 | 18:41 | 0:04 | Voltage difference | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT14 | 1 | BOC | 19:42 | 19:46 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT14 | 1 | GA INT | 11:57 | 13:00 | 1:03 | Internal Shutdown | IG01 | Internal shutdown | Feeeder 1 shutdown taken on emergency basis for fault rectification of feeder 2.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 13:00 | 13:13 | 0:13 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charged WTG auto restarted.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT14 | 1 | BOC | 9:33 | 9:37 | 0:04 | Cut out wind | 21006 | Safety chain - Overpower detected by SINEAX. | Auto reset WTG due to wind beyond limit 20m/s.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT14 | 1 | FORCE MAJEURE | 10:19 | 10:54 | 0:35 | Covid 19 | 0 | Grid Loss | Delay due to facing pandemic condition covid 19 ,checked CC100 panel ACB found ok, then Start WTG.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT14 | 1 | BOC | 14:36 | 14:40 | 0:04 | Cut out wind | 21006 | Safety chain - Overpower detected by SINEAX. | Auto reset WTG due to wind beyond limit 20m/s.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT14 | 1 | GA INT | 8:12 | 8:22 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked and feeder charged.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 8:22 | 8:26 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto reseted after feeder no 1 charge.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT14 | 1 | WTG | 11:29 | 11:42 | 0:13 | Special Activity |  |  | Visually blade inspection done by binacular, then start WTG.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 2:50 | 3:18 | 0:28 | Breakdown Maintenance | 21012 | Safety chain - Rotor brake closed. | Reboot PLC ,checked related circuits and start WTG.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT15 | 1 | BOC | 9:36 | 9:40 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Error comes due to grid voltage fluctuation, WTG autorestarted
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 14:25 | 14:49 | 0:24 | Special Activity | SA14 | Special Activity - WTG Critical Points Checking | Topup coolent in CCU and bottom 5S work done
Giriraj Enterprises | 2021-04-08 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 2:54 | 3:20 | 0:26 | Breakdown Maintenance | 3016 | Rotor brake is closed. | Checked related circuit, reboot PLC , then start WTG.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT15 | 1 | GA INT | 3:34 | 3:48 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 3:48 | 3:52 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | After feeder charged WTG auto reset.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT15 | 1 | GA EXT | 17:32 | 18:38 | 1:06 | External Breakdown | EG02 | Grid Breakdown | GSS transformer Tripped checked and charged from substation.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 18:38 | 18:56 | 0:18 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | WTG manually restarted after feeder charged.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT15 | 1 | GA EXT | 22:16 | 22:26 | 0:10 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken for load changing purpose by EB.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 22:26 | 22:30 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT15 | 1 | GA INT | 9:38 | 16:21 | 6:43 | Internal shutdown | IG01 | Internal shutdown | Internal line shoutdown taken for line maintence from site to nerele village.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 16:21 | 16:32 | 0:11 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT15 | 1 | GA INT | 7:43 | 11:43 | 4:00 | Internal shutdown | IG01 | Internal shutdown | Internal line shutdown taken for line maintenance from site to Phuphere Isolator.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 11:43 | 11:54 | 0:11 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT15 | 1 | GA EXT | 9:11 | 17:17 | 8:06 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken by EB for GSS pre mansoon maintenance work.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 17:17 | 17:27 | 0:10 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Bhendewade | BHT15 | 1 | GA INT | 1:02 | 1:16 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 1:16 | 1:20 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT15 | 1 | GA INT | 17:30 | 17:51 | 0:21 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 17:51 | 17:55 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG autorestarted after feeder charged.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT15 | 1 | BOC | 18:05 | 18:09 | 0:04 | Voltage difference | 7139 | Converter GSA: DC-Bus Hardware Overvoltage Fault | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT15 | 1 | BOC | 18:18 | 18:22 | 0:04 | Voltage difference | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT15 | 1 | BOC | 18:37 | 18:41 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT15 | 1 | GA INT | 11:57 | 13:00 | 1:03 | Internal Shutdown | IG01 | Internal shutdown | Feeeder 1 shutdown taken on emergency basis for fault rectification of feeder 2.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 13:00 | 13:04 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charged WTG auto restarted.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 16:14 | 16:47 | 0:33 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reboot PLC and then start WTG
Giriraj Enterprises | 2021-05-15 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 15:22 | 15:26 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | WTG auto reseted.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT15 | 1 | BOC | 7:49 | 7:53 | 0:04 | Cut out wind | 21006 | Safety chain - Overpower detected by SINEAX. | Auto reset WTG due to wind beyond limit 20m/s.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT15 | 1 | BOC | 9:00 | 9:04 | 0:04 | Cut out wind | 21006 | Safety chain - Overpower detected by SINEAX. | Auto reset WTG due to wind beyond limit 20m/s.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT15 | 1 | BOC | 10:19 | 10:23 | 0:04 | Voltage difference | 30007 | Each YCD shows internal errors. | WTG auto reseted due to grid voltage fluctuation.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT15 | 1 | BOC | 11:27 | 11:31 | 0:04 | Cut out wind | 21006 | Safety chain - Overpower detected by SINEAX. | Auto reset WTG due to wind beyond limit 20m/s.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT15 | 1 | BOC | 19:14 | 19:18 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | WTG auto reseted due to grid voltage fluctuation.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT15 | 1 | GA INT | 8:12 | 8:22 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked and feeder charged.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 8:22 | 8:26 | 0:04 | Breakdown Maintenance | 7009 | Converter LSA: Low line fault | WTG auto reseted after feeder no 1 charge.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT15 | 1 | WTG | 12:36 | 12:42 | 0:06 | Special Activity |  |  | Visually blade inspection done by binacular, then start WTG.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 10:48 | 13:00 | 2:12 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Found yaw brake coil stud is broken in state ,so replaced it and start WTG.
Giriraj Enterprises | 2021-04-03 | Maharashtra | Bhendewade | BHT17 | 2 | BOC | 5:37 | 5:41 | 0:04 | Voltage difference | 7391 | Converter GSA: Inverter System Fault | Error comes due to grid voltage fluctuation, WTG auto restarted.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 16:12 | 16:22 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 16:22 | 16:40 | 0:18 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | WTG manually restarted after feeder charged.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT17 | 2 | GA EXT | 9:36 | 12:06 | 2:30 | External Breakdown | EG02 | Grid Breakdown | Found Y-phase LA of TS feeder 2 at Rile GSS faulty so replaced LA and feeder charged
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 12:06 | 12:10 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | After feeder charged WTG autoreseted
Giriraj Enterprises | 2021-04-07 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 14:29 | 15:06 | 0:37 | Special Activity | SA14 | Special Activity - WTG Critical Points Checking | Top up coolent in CCU, pending point clearance work and bottom 5S work done,
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT17 | 2 | BOC | 3:35 | 3:39 | 0:04 | Voltage difference | 7534 | Converter system detected line voltage error. | Error comes due to grid voltage fluctuation, WTG auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 7:40 | 7:44 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto reset.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 8:32 | 8:43 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 8:43 | 8:47 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | After feeder charged WTG auto reset.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 15:01 | 15:05 | 0:04 | Breakdown Maintenance | 4019 | Stator breaker undervoltage release feedback is not matching the command. | WTG auto reset.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 6:01 | 6:09 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto restarted.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT17 | 2 | GA EXT | 17:32 | 18:38 | 1:06 | External Breakdown | EG02 | Grid Breakdown | GSS transformer Tripped checked and charged from substation.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 18:38 | 18:42 | 0:04 | Breakdown Maintenance | 7008 | Converter LSA: High line fault | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT17 | 2 | GA EXT | 22:16 | 22:26 | 0:10 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken for load changing purpose by EB.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 22:26 | 22:30 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 8:12 | 8:28 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 8:28 | 8:32 | 0:04 | Breakdown Maintenance | 7009 | Converter LSA: Low line fault | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 15:10 | 15:22 | 0:12 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto reset.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 9:44 | 16:20 | 6:36 | Internal shutdown | IG01 | Internal shutdown | Internal line shoutdown taken for line maintence from site to nerele village.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 16:20 | 16:32 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 7:49 | 11:42 | 3:53 | Internal shutdown | IG01 | Internal shutdown | Internal line shutdown taken for line maintenance from site to Phuphere Isolator.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 11:42 | 11:54 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT17 | 2 | GA EXT | 9:11 | 17:17 | 8:06 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken by EB for GSS pre mansoon maintenance work.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 17:17 | 17:29 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Bhendewade | BHT17 | 2 | BOC | 20:30 | 20:34 | 0:04 | Voltage Difference | 7139 | Converter GSA: DC-Bus Hardware Overvoltage Fault | Error comes due to grid voltage fluctuation, WTG auto reset.
Giriraj Enterprises | 2021-04-23 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 5:00 | 5:04 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto restarted.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Bhendewade | BHT17 | 2 | FORCE MAJEURE | 1:37 | 12:19 | 10:42 | Covid 19 | 30009 | Maximum time for yaw positioning exceeded. | O & M team infected due to Covid-19 Pandemic, so delay for attain, remove cable twist and start WTG.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 12:15 | 12:23 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto restarted.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Bhendewade | BHT17 | 2 | FORCE MAJEURE | 23:05 | 24:00 | 0:55 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | O & M team infected due to Covid-19 Pandemic, WIP.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Bhendewade | BHT17 | 2 | FORCE MAJEURE | 0:00 | 10:51 | 10:51 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | O & M team infected due to Covid-19 Pandemic, so delay for attain, remove cable twist and start WTG.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 17:02 | 17:06 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | WTG auto restarted.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 20:26 | 20:30 | 0:04 | Breakdown Maintenance | 4019 | Stator breaker undervoltage release feedback is not matching the command. | WTG auto restarted.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 15:50 | 15:54 | 0:04 | Breakdown Maintenance | 4019 | Stator breaker undervoltage release feedback is not matching the command. | WTG auto restarted.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 16:10 | 16:14 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto restarted.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Bhendewade | BHT17 | 2 | FORCE MAJEURE | 11:34 | 11:50 | 0:16 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | O & M team infected due to Covid-19 Pandemic, so delay for reset WTG
Giriraj Enterprises | 2021-04-30 | Maharashtra | Bhendewade | BHT17 | 2 | FORCE MAJEURE | 12:05 | 12:28 | 0:23 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | O & M team infected due to Covid-19 Pandemic, so delay for reset WTG.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Bhendewade | BHT17 | 2 | FORCE MAJEURE | 7:27 | 9:01 | 1:34 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | O & M team infected due to Covid-19 Pandemic, delay for attained WTG, clean yaw sliding pad by acetone and start WTG.
Giriraj Enterprises | 2021-05-02 | Maharashtra | Bhendewade | BHT17 | 2 | FORCE MAJEURE | 0:00 | 6:51 | 6:51 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | O & M team infected due to Covid-19 Pandemic,delay for attain WTG, set (YCD) twist stop sensor limit switch and reset WTG.
Giriraj Enterprises | 2021-05-02 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 17:40 | 18:03 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok
Giriraj Enterprises | 2021-05-02 | Maharashtra | Bhendewade | BHT17 | 2 | FORCE MAJEURE | 18:03 | 19:09 | 1:06 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | O & M team infected due to Covid-19 Pandemic,delay for attain WTG, yaw shielding done, YCD limit switch setting done, then start WTG.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 13:26 | 13:54 | 0:28 | Breakdown Maintenance | 21013 | Safety chain - Blade working position exceeded. | WTG auto restarted.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 16:17 | 16:33 | 0:16 | Breakdown Maintenance | 21013 | Safety chain - Blade working position exceeded. | WTG auto restarted.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 11:47 | 12:08 | 0:21 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 12:08 | 12:12 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG autorestarted after feeder charged.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 11:44 | 11:48 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT17 | 2 | BOC | 18:07 | 18:11 | 0:04 | Voltage difference | 7009 | Converter LSA: Low line fault | Due to Grid Voltage Fluctuations of feeder no 2 jark error come, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT17 | 2 | BOC | 18:19 | 18:23 | 0:04 | Voltage difference | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Due to Grid Voltage Fluctuations of feeder no 2 jark error come, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 18:25 | 18:29 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 18:38 | 24:00 | 5:22 | Feeder tripped E/F | IG02 | Earth Fault | Due to heavy rain and lightning feeder 2 petrolling is in WIP.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 0:00 | 13:00 | 13:00 | Feeder Tripped E/F | IG02 | Earth Fault | Feeder 2 R phase pin insulator faulty near durugewade village ,so replaced it and charged feeder.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 13:00 | 13:20 | 0:20 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | After feeder charged WTG auto restarted.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 8:59 | 9:11 | 0:12 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto restarted.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 17:43 | 17:47 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | WTG auto restarted.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 18:33 | 18:37 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | WTG auto restarted.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 18:15 | 18:19 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | WTG auto restarted.
Giriraj Enterprises | 2021-05-14 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 17:13 | 17:21 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG auto reseted.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 14:44 | 14:48 | 0:04 | Breakdown Maintenance | 24001 | Drive train swinging. | WTG auto reseted.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT17 | 2 | BOC | 10:20 | 10:24 | 0:04 | Voltage difference | 30007 | Each YCD shows internal errors. | WTG auto reseted due to grid voltage fluctuation.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 11:31 | 11:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked and feeder charged.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 11:40 | 11:44 | 0:04 | Breakdown Maintenance | 7137 | Converter GSA: Low line fault | WTG auto reseted after feeder charge.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT17 | 2 | BOC | 19:15 | 19:19 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | WTG auto reseted due to grid voltage fluctuation.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT17 | 2 | BOC | 21:18 | 21:22 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | WTG auto reseted due to grid voltage fluctuation.
Giriraj Enterprises | 2021-05-17 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 7:55 | 7:59 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | WTG auto restarted.
Giriraj Enterprises | 2021-05-17 | Maharashtra | Bhendewade | BHT17 | 2 | GA INT | 14:10 | 14:50 | 0:40 | WTG | IG05 | Section Isolator Open | Section isolator open for fault rectification of jump open of Y phase near BHT18.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT17 | 2 | WTG | 12:41 | 12:48 | 0:07 | Special Activity |  |  | Visually blade inspection done by binacular, then start WTG.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 10:10 | 10:53 | 0:43 | Special Activity | SA14 | Special Activity - WTG Critical Points Checking | WTG bottom cleaning work done and start WTG.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 16:12 | 16:22 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 16:22 | 16:26 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT31 | 2 | GA EXT | 9:36 | 12:06 | 2:30 | External Breakdown | EG02 | Grid Breakdown | Found Y-phase LA of TS feeder 2 at Rile GSS faulty so replaced LA and feeder charged
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 12:06 | 12:21 | 0:15 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | After feeder charged WTG autoreseted
Giriraj Enterprises | 2021-04-06 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 15:19 | 15:26 | 0:07 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Check and reset WTG
Giriraj Enterprises | 2021-04-09 | Maharashtra | Bhendewade | BHT31 | 2 | BOC | 3:35 | 3:39 | 0:04 | Voltage difference | 7534 | Converter system detected line voltage error. | Error comes due to grid voltage fluctuation, WTG auto reset.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 8:32 | 8:43 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 8:43 | 8:47 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | After feeder charged WTG auto reset.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT31 | 2 | GA EXT | 17:32 | 18:38 | 1:06 | External Breakdown | EG02 | Grid Breakdown | GSS transformer Tripped checked and charged from substation.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 18:38 | 18:53 | 0:15 | Breakdown Maintenance | 7136 | Converter GSA: High line fault | WTG manually restarted after feeder charged.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT31 | 2 | GA EXT | 22:16 | 22:26 | 0:10 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken for load changing purpose by EB.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 22:26 | 22:30 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 8:12 | 8:28 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 8:28 | 8:32 | 0:04 | Breakdown Maintenance | 7009 | Converter LSA: Low line fault | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 9:44 | 16:20 | 6:36 | Internal shutdown | IG01 | Internal shutdown | Internal line shoutdown taken for line maintence from site to nerele village.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 16:20 | 16:32 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 7:49 | 11:42 | 3:53 | Internal shutdown | IG01 | Internal shutdown | Internal line shutdown taken for line maintenance from site to Phuphere Isolator.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 11:42 | 11:54 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT31 | 2 | GA EXT | 9:11 | 17:17 | 8:06 | External Shutdown | EG01 | Grid Shutdown | Shutdown taken by EB for GSS pre mansoon maintenance work.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 17:17 | 17:29 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-05-02 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 17:40 | 18:03 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok
Giriraj Enterprises | 2021-05-02 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 18:03 | 18:11 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WTG auto restarted after feeder charged.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 11:47 | 12:08 | 0:21 | Feeder tripped E/F | IG02 | Earth Fault | Checked and charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 12:08 | 12:19 | 0:11 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG autorestarted after feeder charged.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT31 | 2 | BOC | 18:07 | 18:11 | 0:04 | Voltage difference | 7009 | Converter LSA: Low line fault | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT31 | 2 | BOC | 18:19 | 18:23 | 0:04 | Voltage difference | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Due to Grid Voltage Fluction of feeder no 2 jark, WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 18:38 | 24:00 | 5:22 | Feeder tripped E/F | IG02 | Earth Fault | Due to heavy rain and lightning feeder 2 petrolling is in WIP.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 0:00 | 13:00 | 13:00 | Feeder Tripped E/F | IG02 | Earth Fault | Feeder 2 R phase pin insulator faulty near durugewade village ,so replaced it and charged feeder.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 13:00 | 13:12 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charged WTG auto restarted.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT31 | 2 | GA INT | 11:31 | 11:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked and feeder charged.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 11:40 | 11:44 | 0:04 | Breakdown Maintenance | 7137 | Converter GSA: Low line fault | WTG auto reseted after feeder charge.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT31 | 2 | BOC | 15:02 | 15:06 | 0:04 | Cut out wind | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset WTG due to wind beyond limit 20m/s.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT31 | 2 | BOC | 15:56 | 16:00 | 0:04 | Cut out wind | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset WTG due to wind beyond limit 20m/s.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT31 | 2 | BOC | 17:07 | 17:11 | 0:04 | Cut out wind | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset WTG due to wind beyond limit 20m/s.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Bhendewade | BHT31 | 2 | BOC | 19:15 | 19:19 | 0:04 | Voltage difference | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | WTG auto reseted due to grid voltage fluctuation.
Giriraj Enterprises | 2021-05-17 | Maharashtra | Bhendewade | BHT31 | 2 | WTG | 3:05 | 12:03 | 8:58 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Replaced accumulator manifold, checked hydraulic related connection & start WTG.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Bhendewade | BHT31 | 2 | FORCE MAJEURE | 17:46 | 19:51 | 2:05 | Covid 19 | 0 | Grid Loss | Checked CC100 panel ACB working found ok, then Start WTG (Delay due to facing pandemic condition covid 19).
DJ Malpani - Palakkad | 2021-04-01 | Kerala | Palakkad | DJM01 | 1 | WTG | 0:40 | 18:26 | 17:46 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | After Bypass ACB Start WTG
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM01 | 1 | GA INT | 13:09 | 15:48 | 2:39 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM01 | 1 | WTG | 16:08 | 18:12 | 2:04 | Breakdown Maintenance | 7527 | Converter stator synchronization failed. | Check related connection all ok and Update DSP After stable Grid voltage Start WTG
DJ Malpani - Palakkad | 2021-04-03 | Kerala | Palakkad | DJM01 | 1 | WTG | 22:49 | 23:59 | 1:10 | Breakdown Maintenance | 21009 | Safety chain - Overspeed detected by overspeed relay. | WIP
DJ Malpani - Palakkad | 2021-04-04 | Kerala | Palakkad | DJM01 | 1 | WTG | 0:00 | 1:02 | 1:02 | Breakdown Maintenance | 21009 | Safety chain - Overspeed detected by overspeed relay. | Attend turbine check related connection found than Start WTG
DJ Malpani - Palakkad | 2021-04-06 | Kerala | Palakkad | DJM01 | 1 | WTG | 4:48 | 4:52 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-06 | Kerala | Palakkad | DJM01 | 1 | WTG | 15:27 | 15:38 | 0:11 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM01 | 1 | WTG | 3:34 | 3:38 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM01 | 1 | WTG | 9:26 | 9:34 | 0:08 | Breakdown Maintenance | 23008 | Hub healthcheck timeout. | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM01 | 1 | WTG | 10:09 | 12:45 | 2:36 | Breakdown Maintenance | 3016 | Rotor brake is closed. | Attend turbine check related connection found relay malfuntion after replace relay Start WTG
DJ Malpani - Palakkad | 2021-04-10 | Kerala | Palakkad | DJM01 | 1 | WTG | 14:41 | 14:45 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto Reset
DJ Malpani - Palakkad | 2021-04-12 | Kerala | Palakkad | DJM01 | 1 | WTG | 15:40 | 15:48 | 0:08 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-04-13 | Kerala | Palakkad | DJM01 | 1 | WTG | 17:31 | 19:45 | 2:14 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | attend turbine check and found Relay malfunction after correct start WTG
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM01 | 1 | WTG | 3:11 | 3:15 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-16 | Kerala | Palakkad | DJM01 | 1 | WTG | 18:28 | 18:56 | 0:28 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Check and found VCB trip due to grid fluctuation After charge VCB Start WTG
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM01 | 1 | WTG | 10:09 | 10:13 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto Reset
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM01 | 1 | GA INT | 16:43 | 17:59 | 1:16 | Feeder tripped E/F | IG02 | Earth Fault | Check and found B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM01 | 1 | WTG | 17:59 | 20:28 | 2:29 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Attend turbine and check related connection than Start WTG
DJ Malpani - Palakkad | 2021-04-22 | Kerala | Palakkad | DJM01 | 1 | WTG | 18:02 | 18:19 | 0:17 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | VCB trip after VCB charged and start the WTG
DJ Malpani - Palakkad | 2021-04-24 | Kerala | Palakkad | DJM01 | 1 | WTG | 15:52 | 15:56 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset
DJ Malpani - Palakkad | 2021-04-29 | Kerala | Palakkad | DJM01 | 1 | WTG | 18:06 | 18:10 | 0:04 | Breakdown Maintenance | 23006 | Converter healthcheck timeout. | Auto Reset
DJ Malpani - Palakkad | 2021-04-29 | Kerala | Palakkad | DJM01 | 1 | WTG | 18:59 | 19:30 | 0:31 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Check and found VCB trip due to grid fluctuation After charge VCB Start WTG
DJ Malpani - Palakkad | 2021-05-02 | Kerala | Palakkad | DJM01 | 1 | WTG | 6:35 | 6:39 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-04 | Kerala | Palakkad | DJM01 | 1 | WTG | 22:01 | 22:05 | 0:04 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM01 | 1 | WTG | 6:58 | 7:30 | 0:32 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM01 | 1 | WTG | 4:49 | 4:53 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM01 | 1 | GA INT | 11:35 | 15:43 | 4:08 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B DO fuse failure and replaced ,then R,Y,B conductor replaced work complete after charge feeder
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM01 | 1 | WTG | 15:43 | 15:51 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charge Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM01 | 1 | WTG | 4:56 | 5:08 | 0:12 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-13 | Kerala | Palakkad | DJM01 | 1 | WTG | 9:34 | 10:27 | 0:53 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Reboot and write read converter perameter than Start WTG (Due to Grid Fluction on FD No 1)
DJ Malpani - Palakkad | 2021-05-14 | Kerala | Palakkad | DJM01 | 1 | WTG | 11:09 | 11:13 | 0:04 | Breakdown Maintenance | 4111 | CC101 cooling fan feedback alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM01 | 1 | WTG | 14:41 | 16:58 | 2:17 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | After charge VCB Write Read Converter perameter Than Start WTG(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-05-16 | Kerala | Palakkad | DJM01 | 1 | WTG | 11:03 | 11:07 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM02 | 1 | GA INT | 13:09 | 15:48 | 2:39 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM02 | 1 | WTG | 16:03 | 16:42 | 0:39 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | After stable Grid Voltage Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-05 | Kerala | Palakkad | DJM02 | 1 | WTG | 1:31 | 1:35 | 0:04 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-05 | Kerala | Palakkad | DJM02 | 1 | WTG | 17:02 | 17:06 | 0:04 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-04-06 | Kerala | Palakkad | DJM02 | 1 | WTG | 6:57 | 7:01 | 0:04 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-06 | Kerala | Palakkad | DJM02 | 1 | WTG | 18:05 | 18:09 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM02 | 1 | WTG | 3:36 | 4:16 | 0:40 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM02 | 1 | WTG | 4:13 | 4:17 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM02 | 1 | WTG | 18:27 | 18:53 | 0:26 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-08 | Kerala | Palakkad | DJM02 | 1 | WTG | 17:57 | 18:28 | 0:31 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-09 | Kerala | Palakkad | DJM02 | 1 | WTG | 14:46 | 19:24 | 4:38 | Breakdown Maintenance | SA17 | Special Activity - Repeated error rectification | Attend turbine found yaw motor brake pad worn out after replace pad Start WTG
DJ Malpani - Palakkad | 2021-04-10 | Kerala | Palakkad | DJM02 | 1 | WTG | 13:15 | 13:19 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-10 | Kerala | Palakkad | DJM02 | 1 | WTG | 18:15 | 18:19 | 0:04 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-11 | Kerala | Palakkad | DJM02 | 1 | WTG | 13:17 | 13:21 | 0:04 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-12 | Kerala | Palakkad | DJM02 | 1 | WTG | 15:32 | 15:36 | 0:04 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-12 | Kerala | Palakkad | DJM02 | 1 | WTG | 18:43 | 18:51 | 0:08 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-04-13 | Kerala | Palakkad | DJM02 | 1 | WTG | 18:07 | 18:11 | 0:04 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM02 | 1 | WTG | 3:03 | 3:07 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM02 | 1 | WTG | 23:00 | 23:08 | 0:08 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM02 | 1 | WTG | 6:19 | 6:35 | 0:16 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM02 | 1 | WTG | 16:27 | 20:29 | 4:02 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Attend turbine check and found yaw converter malfunction after check all related connection Start WTG
DJ Malpani - Palakkad | 2021-04-16 | Kerala | Palakkad | DJM02 | 1 | WTG | 5:43 | 5:47 | 0:04 | Breakdown Maintenance | 12070 | Blade 2: Blade state plausibility. | Auto Reset
DJ Malpani - Palakkad | 2021-04-16 | Kerala | Palakkad | DJM02 | 1 | WTG | 18:18 | 18:32 | 0:14 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-16 | Kerala | Palakkad | DJM02 | 1 | WTG | 21:49 | 22:36 | 0:47 | Breakdown Maintenance | 7012 | Converter LSA: Power supply fault 24V | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM02 | 1 | GA INT | 16:43 | 17:59 | 1:16 | Feeder tripped E/F | IG02 | Earth Fault | Check and found B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM02 | 1 | WTG | 17:59 | 19:30 | 1:31 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Check and found Transformer HV side Y phase bimetallic connector worn out after Replace Start WTG
DJ Malpani - Palakkad | 2021-04-21 | Kerala | Palakkad | DJM02 | 1 | WTG | 7:23 | 7:35 | 0:12 | Breakdown Maintenance | 12070 | Blade 2: Blade state plausibility. | Auto Reset
DJ Malpani - Palakkad | 2021-04-23 | Kerala | Palakkad | DJM02 | 1 | WTG | 19:31 | 19:35 | 0:04 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-04-24 | Kerala | Palakkad | DJM02 | 1 | WTG | 19:09 | 19:17 | 0:08 | Breakdown Maintenance | 31021 | Blade teeth lubrication is in maintenance state. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM02 | 1 | WTG | 5:02 | 5:06 | 0:04 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-27 | Kerala | Palakkad | DJM02 | 1 | WTG | 19:14 | 19:18 | 0:04 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-04-29 | Kerala | Palakkad | DJM02 | 1 | WTG | 18:49 | 18:53 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset
DJ Malpani - Palakkad | 2021-04-29 | Kerala | Palakkad | DJM02 | 1 | WTG | 23:51 | 23:55 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto Reset
DJ Malpani - Palakkad | 2021-04-30 | Kerala | Palakkad | DJM02 | 1 | WTG | 14:26 | 14:30 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto Reset
DJ Malpani - Palakkad | 2021-04-30 | Kerala | Palakkad | DJM02 | 1 | WTG | 19:15 | 19:19 | 0:04 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-01 | Kerala | Palakkad | DJM02 | 1 | WTG | 14:10 | 14:18 | 0:08 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-05-02 | Kerala | Palakkad | DJM02 | 1 | WTG | 3:58 | 4:06 | 0:08 | Breakdown Maintenance | 1003 | Anemometer 1 communication error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-03 | Kerala | Palakkad | DJM02 | 1 | WTG | 19:17 | 19:25 | 0:08 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-04 | Kerala | Palakkad | DJM02 | 1 | WTG | 23:51 | 23:59 | 0:08 | Breakdown Maintenance | 12070 | Blade 2: Blade state plausibility. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM02 | 1 | WTG | 1:12 | 1:20 | 0:08 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM02 | 1 | WTG | 7:00 | 7:28 | 0:28 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM02 | 1 | WTG | 15:06 | 15:10 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM02 | 1 | WTG | 19:21 | 19:25 | 0:04 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM02 | 1 | WTG | 8:42 | 8:50 | 0:08 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM02 | 1 | GA INT | 11:35 | 15:43 | 4:08 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B DO fuse failure and replaced ,then R,Y,B conductor replaced work complete after charge feeder
DJ Malpani - Palakkad | 2021-05-08 | Kerala | Palakkad | DJM02 | 1 | WTG | 14:29 | 14:55 | 0:26 | Breakdown Maintenance | 12052 | Blade 1: Brake has not opened in Reference Mode. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-08 | Kerala | Palakkad | DJM02 | 1 | WTG | 15:12 | 16:36 | 1:24 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Attend turbine and check related connection than Start WTG
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM02 | 1 | WTG | 4:52 | 4:56 | 0:04 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM02 | 1 | WTG | 16:57 | 23:51 | 6:54 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Attend turbine and check and tighten all related connection than Start WTG
DJ Malpani - Palakkad | 2021-05-10 | Kerala | Palakkad | DJM02 | 1 | WTG | 14:38 | 14:42 | 0:04 | Breakdown Maintenance | 7012 | Converter LSA: Power supply fault 24V | Auto Reset (Due to Grid Fluction on FD No 1)
DJ Malpani - Palakkad | 2021-05-10 | Kerala | Palakkad | DJM02 | 1 | WTG | 18:28 | 18:32 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-10 | Kerala | Palakkad | DJM02 | 1 | WTG | 23:17 | 23:25 | 0:08 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-05-11 | Kerala | Palakkad | DJM02 | 1 | WTG | 1:34 | 9:03 | 7:29 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Attend turbine and check and tighten all related connection than Start WTG
DJ Malpani - Palakkad | 2021-05-11 | Kerala | Palakkad | DJM02 | 1 | WTG | 18:12 | 24:00 | 5:48 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Attend turbine and check and tighten all related connection than Start WTG
DJ Malpani - Palakkad | 2021-05-12 | Kerala | Palakkad | DJM02 | 1 | WTG | 0:00 | 22:45 | 22:45 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Replace GB slipring WIP……
DJ Malpani - Palakkad | 2021-05-13 | Kerala | Palakkad | DJM02 | 1 | WTG | 0:00 | 18:36 | 18:36 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Check and connection interchange k9.1 relay and use 24v spare cable Nacelle to OVP panel than start WTG
DJ Malpani - Palakkad | 2021-05-14 | Kerala | Palakkad | DJM02 | 1 | WTG | 13:07 | 13:11 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM02 | 1 | WTG | 6:09 | 6:50 | 0:41 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM02 | 1 | WTG | 14:31 | 14:47 | 0:16 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Reset and Start WTG(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-05-16 | Kerala | Palakkad | DJM02 | 1 | WTG | 10:54 | 11:10 | 0:16 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Reset and Start WTG(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-05-16 | Kerala | Palakkad | DJM02 | 1 | WTG | 12:00 | 12:04 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-18 | Kerala | Palakkad | DJM02 | 1 | WTG | 5:36 | 5:56 | 0:20 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-19 | Kerala | Palakkad | DJM02 | 1 | WTG | 20:49 | 20:53 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-20 | Kerala | Palakkad | DJM02 | 1 | WTG | 0:55 | 0:59 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM03 | 1 | GA INT | 13:09 | 15:48 | 2:39 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM03 | 1 | WTG | 16:08 | 16:25 | 0:17 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | After stable Grid Voltage Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-06 | Kerala | Palakkad | DJM03 | 1 | WTG | 16:17 | 16:50 | 0:33 | Breakdown Maintenance | 12080 | Blade 2: Error at referencing. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM03 | 1 | WTG | 0:55 | 3:46 | 2:51 | Breakdown Maintenance | 12074 | Blade 2: IPS was not active in feathering position. | Check related connection than Start WTG
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM03 | 1 | WTG | 11:41 | 13:45 | 2:04 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Check related connection than reboot and Start WTG
DJ Malpani - Palakkad | 2021-04-10 | Kerala | Palakkad | DJM03 | 1 | WTG | 16:12 | 17:33 | 1:21 | Breakdown Maintenance | 12080 | Blade 2: Error at referencing. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-11 | Kerala | Palakkad | DJM03 | 1 | WTG | 1:39 | 1:59 | 0:20 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-12 | Kerala | Palakkad | DJM03 | 1 | WTG | 5:41 | 5:47 | 0:06 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-13 | Kerala | Palakkad | DJM03 | 1 | WTG | 15:37 | 15:44 | 0:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM03 | 1 | WTG | 14:24 | 14:28 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM03 | 1 | GA INT | 16:43 | 17:59 | 1:16 | Feeder tripped E/F | IG02 | Earth Fault | Check and found B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-21 | Kerala | Palakkad | DJM03 | 1 | WTG | 18:47 | 19:22 | 0:35 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | VCB trip after VCB charged and start the WTG
DJ Malpani - Palakkad | 2021-04-24 | Kerala | Palakkad | DJM03 | 1 | WTG | 15:23 | 15:36 | 0:13 | Breakdown Maintenance | 7012 | Converter LSA: Power supply fault 24V | Reset and Start WTG (Due to Grid Fluction on FD No 1)
DJ Malpani - Palakkad | 2021-04-29 | Kerala | Palakkad | DJM03 | 1 | WTG | 18:37 | 18:41 | 0:04 | Breakdown Maintenance | 7398 | Converter GSA: Stator voltage feedback fault. | Reset and Start WTG (Due to Grid Fluction on FD No 1)
DJ Malpani - Palakkad | 2021-05-01 | Kerala | Palakkad | DJM03 | 1 | WTG | 17:50 | 18:14 | 0:24 | Breakdown Maintenance | 12074 | Blade 2: IPS was not active in feathering position. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-02 | Kerala | Palakkad | DJM03 | 1 | WTG | 2:01 | 2:05 | 0:04 | Breakdown Maintenance | 12074 | Blade 2: IPS was not active in feathering position. | Auto Reset
DJ Malpani - Palakkad | 2021-05-02 | Kerala | Palakkad | DJM03 | 1 | WTG | 16:34 | 17:06 | 0:32 | Breakdown Maintenance | 12080 | Blade 2: Error at referencing. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-03 | Kerala | Palakkad | DJM03 | 1 | WTG | 20:28 | 20:35 | 0:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-03 | Kerala | Palakkad | DJM03 | 1 | WTG | 20:49 | 21:05 | 0:16 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-04 | Kerala | Palakkad | DJM03 | 1 | WTG | 21:27 | 21:31 | 0:04 | Breakdown Maintenance | 12074 | Blade 2: IPS was not active in feathering position. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM03 | 1 | WTG | 3:48 | 4:21 | 0:33 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM03 | 1 | WTG | 15:50 | 15:54 | 0:04 | Breakdown Maintenance | 12074 | Blade 2: IPS was not active in feathering position. | Auto Reset
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM03 | 1 | WTG | 17:23 | 18:12 | 0:49 | Breakdown Maintenance | 12080 | Blade 2: Error at referencing. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM03 | 1 | GA INT | 11:35 | 15:43 | 4:08 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B DO fuse failure and replaced ,then R,Y,B conductor replaced work complete after charge feeder
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM03 | 1 | WTG | 20:05 | 20:09 | 0:04 | Breakdown Maintenance | 12074 | Blade 2: IPS was not active in feathering position. | Auto Reset
DJ Malpani - Palakkad | 2021-05-08 | Kerala | Palakkad | DJM03 | 1 | WTG | 19:26 | 19:40 | 0:14 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-08 | Kerala | Palakkad | DJM03 | 1 | WTG | 19:53 | 20:50 | 0:57 | Breakdown Maintenance | 12080 | Blade 2: Error at referencing. | Attend turbine and check Proximity sensor and plate related connetion and start WTG.
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM03 | 1 | WTG | 1:08 | 1:37 | 0:29 | Breakdown Maintenance | 12074 | Blade 2: IPS was not active in feathering position. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM03 | 1 | WTG | 14:56 | 15:44 | 0:48 | Breakdown Maintenance | 12080 | Blade 2: Error at referencing. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM03 | 1 | WTG | 15:47 | 16:08 | 0:21 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-10 | Kerala | Palakkad | DJM03 | 1 | WTG | 13:05 | 13:09 | 0:04 | Breakdown Maintenance | 12074 | Blade 2: IPS was not active in feathering position. | Auto Reset
DJ Malpani - Palakkad | 2021-05-12 | Kerala | Palakkad | DJM03 | 1 | WTG | 11:51 | 11:55 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset
DJ Malpani - Palakkad | 2021-05-13 | Kerala | Palakkad | DJM03 | 1 | WTG | 9:31 | 9:59 | 0:28 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Reboot and write read converter perameter than Start WTG (Due to Grid Fluction on FD No 1)
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM03 | 1 | WTG | 14:39 | 15:10 | 0:31 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Reset and Start WTG(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-05-16 | Kerala | Palakkad | DJM03 | 1 | WTG | 11:05 | 15:07 | 4:02 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Check and found tranformer HV side bimetalic conductor broken after Replace Start WTG(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-04-01 | Kerala | Palakkad | DJM05 | 1 | WTG | 16:22 | 16:26 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto Reset
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM05 | 1 | GA INT | 13:09 | 15:48 | 2:39 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM05 | 1 | WTG | 16:42 | 16:47 | 0:05 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | After stable Grid Voltage Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-03 | Kerala | Palakkad | DJM05 | 1 | WTG | 20:39 | 20:43 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM05 | 1 | WTG | 4:02 | 4:10 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM05 | 1 | WTG | 12:11 | 12:19 | 0:08 | Breakdown Maintenance | 7513 | Converter state was precharge for too long time. | Auto Reset
DJ Malpani - Palakkad | 2021-04-08 | Kerala | Palakkad | DJM05 | 1 | WTG | 11:57 | 12:01 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Auto Reset
DJ Malpani - Palakkad | 2021-04-12 | Kerala | Palakkad | DJM05 | 1 | WTG | 16:59 | 17:03 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto Reset
DJ Malpani - Palakkad | 2021-04-13 | Kerala | Palakkad | DJM05 | 1 | WTG | 0:35 | 0:39 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-13 | Kerala | Palakkad | DJM05 | 1 | WTG | 18:15 | 18:19 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto Reset
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM05 | 1 | WTG | 3:31 | 3:39 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM05 | 1 | WTG | 14:22 | 14:26 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset
DJ Malpani - Palakkad | 2021-04-16 | Kerala | Palakkad | DJM05 | 1 | WTG | 18:58 | 19:02 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM05 | 1 | GA INT | 16:43 | 17:59 | 1:16 | Feeder tripped E/F | IG02 | Earth Fault | Check and found B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-24 | Kerala | Palakkad | DJM05 | 1 | WTG | 12:16 | 12:20 | 0:04 | Breakdown Maintenance | 7513 | Converter state was precharge for too long time. | Auto Reset
DJ Malpani - Palakkad | 2021-04-24 | Kerala | Palakkad | DJM05 | 1 | WTG | 15:54 | 15:58 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM05 | 1 | WTG | 5:26 | 5:30 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM05 | 1 | WTG | 7:15 | 7:23 | 0:08 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM05 | 1 | WTG | 8:09 | 8:23 | 0:14 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-29 | Kerala | Palakkad | DJM05 | 1 | WTG | 19:00 | 19:04 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset
DJ Malpani - Palakkad | 2021-05-02 | Kerala | Palakkad | DJM05 | 1 | WTG | 3:53 | 4:05 | 0:12 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM05 | 1 | WTG | 6:11 | 6:15 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM05 | 1 | WTG | 10:48 | 10:52 | 0:04 | Breakdown Maintenance | 4134 | CC101 24VDC buffer module for closing/opening breakers is not charged. | Auto Reset
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM05 | 1 | GA INT | 11:35 | 15:43 | 4:08 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B DO fuse failure and replaced ,then R,Y,B conductor replaced work complete after charge feeder
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM05 | 1 | WTG | 16:57 | 17:05 | 0:08 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM05 | 1 | WTG | 19:26 | 23:59 | 4:33 | Breakdown Maintenance | 7012 | Converter LSA: Power supply fault 24V | WIP
DJ Malpani - Palakkad | 2021-05-08 | Kerala | Palakkad | DJM05 | 1 | WTG | 0:00 | 10:13 | 10:13 | Breakdown Maintenance | 7012 | Converter LSA: Power supply fault 24V | Checked related circuit and replaced ASIM board ,DSP software updated then start WTG.
DJ Malpani - Palakkad | 2021-05-08 | Kerala | Palakkad | DJM05 | 1 | WTG | 18:45 | 18:49 | 0:04 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM05 | 1 | WTG | 6:24 | 6:28 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-10 | Kerala | Palakkad | DJM05 | 1 | WTG | 14:48 | 14:52 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset (Due to Grid Fluction on FD No 1)
DJ Malpani - Palakkad | 2021-05-13 | Kerala | Palakkad | DJM05 | 1 | WTG | 9:33 | 9:37 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset (Due to Grid Fluction on FD No 1)
DJ Malpani - Palakkad | 2021-05-14 | Kerala | Palakkad | DJM05 | 1 | WTG | 15:39 | 15:47 | 0:08 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM05 | 1 | WTG | 14:41 | 15:02 | 0:21 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Reset and Start WTG(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM05 | 1 | WTG | 19:28 | 20:00 | 0:32 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-16 | Kerala | Palakkad | DJM05 | 1 | WTG | 11:03 | 11:11 | 0:08 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Reset and Start WTG(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-04-01 | Kerala | Palakkad | DJM06 | 2 | WTG | 17:38 | 17:42 | 0:04 | Breakdown Maintenance | 22003 | Speed measurement analog rotor speed high error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-01 | Kerala | Palakkad | DJM06 | 2 | GA EXT | 20:04 | 20:25 | 0:21 | External Breakdown | EG02 | Grid Breakdown | Feeder tripped due to 220KV substation side Issue
DJ Malpani - Palakkad | 2021-04-01 | Kerala | Palakkad | DJM06 | 2 | WTG | 20:25 | 20:45 | 0:20 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM06 | 2 | GA EXT | 1:22 | 4:31 | 3:09 | External Breakdown | EG02 | Grid Breakdown | Feeder tripped due to 220KV substation side Issue
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM06 | 2 | GA INT | 13:09 | 15:42 | 2:33 | Internal Shutdown | IG01 | Internal shutdown | Feeder Shutdown taken for safety purpose
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM06 | 2 | WTG | 16:06 | 16:10 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-03 | Kerala | Palakkad | DJM06 | 2 | WTG | 0:13 | 0:29 | 0:16 | Breakdown Maintenance | 22003 | Speed measurement analog rotor speed high error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-03 | Kerala | Palakkad | DJM06 | 2 | WTG | 14:49 | 15:24 | 0:35 | Breakdown Maintenance | 10041 | Generator bearing temperature NDE above error limit. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-03 | Kerala | Palakkad | DJM06 | 2 | WTG | 19:20 | 19:24 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM06 | 2 | WTG | 4:27 | 4:31 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-09 | Kerala | Palakkad | DJM06 | 2 | WTG | 8:34 | 9:40 | 1:06 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-13 | Kerala | Palakkad | DJM06 | 2 | WTG | 12:54 | 12:58 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM06 | 2 | WTG | 2:54 | 3:02 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM06 | 2 | WTG | 10:04 | 11:20 | 1:16 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-16 | Kerala | Palakkad | DJM06 | 2 | WTG | 18:22 | 18:26 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM06 | 2 | GA INT | 16:54 | 17:59 | 1:05 | Internal Shutdown | IG01 | Internal shutdown | Feeder Shutdown taken for safety purpose
DJ Malpani - Palakkad | 2021-04-21 | Kerala | Palakkad | DJM06 | 2 | WTG | 9:02 | 9:06 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-22 | Kerala | Palakkad | DJM06 | 2 | WTG | 12:04 | 12:08 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-23 | Kerala | Palakkad | DJM06 | 2 | WTG | 14:55 | 14:59 | 0:04 | Breakdown Maintenance | 22003 | Speed measurement analog rotor speed high error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM06 | 2 | WTG | 1:58 | 2:06 | 0:08 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM06 | 2 | WTG | 7:14 | 7:18 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM06 | 2 | WTG | 14:07 | 14:11 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-26 | Kerala | Palakkad | DJM06 | 2 | WTG | 13:51 | 13:59 | 0:08 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-28 | Kerala | Palakkad | DJM06 | 2 | WTG | 16:48 | 16:52 | 0:04 | Breakdown Maintenance | 31021 | Blade teeth lubrication is in maintenance state. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-01 | Kerala | Palakkad | DJM06 | 2 | WTG | 11:07 | 12:19 | 1:12 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Attend turbine and check related connection than Start WTG
DJ Malpani - Palakkad | 2021-05-01 | Kerala | Palakkad | DJM06 | 2 | WTG | 12:27 | 12:31 | 0:04 | Breakdown Maintenance | 12006 | Health check error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-02 | Kerala | Palakkad | DJM06 | 2 | WTG | 3:52 | 3:56 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-02 | Kerala | Palakkad | DJM06 | 2 | WTG | 9:36 | 9:40 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-03 | Kerala | Palakkad | DJM06 | 2 | WTG | 0:24 | 1:01 | 0:37 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Attend turbine and check related connection than Start WTG
DJ Malpani - Palakkad | 2021-05-03 | Kerala | Palakkad | DJM06 | 2 | WTG | 13:21 | 13:45 | 0:24 | Breakdown Maintenance | 7012 | Converter LSA: Power supply fault 24V | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-04 | Kerala | Palakkad | DJM06 | 2 | WTG | 11:53 | 12:01 | 0:08 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM06 | 2 | WTG | 5:36 | 5:40 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM06 | 2 | WTG | 18:25 | 18:33 | 0:08 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM06 | 2 | WTG | 16:19 | 16:31 | 0:12 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM06 | 2 | GA EXT | 21:36 | 22:01 | 0:25 | External Breakdown | EG02 | Grid Breakdown | Feeder tripped due to 220KV substation side Issue
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM06 | 2 | WTG | 22:01 | 22:14 | 0:13 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charge Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM06 | 2 | WTG | 9:45 | 10:21 | 0:36 | Breakdown Maintenance | SA17 | Special Activity - Repeated error rectification | Slow stop" stator breaker tripped"- Checked related circuit and spare cable used for stator breaker trip circuit and rest WTG.WTG under observation.
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM06 | 2 | GA INT | 11:50 | 15:43 | 3:53 | Internal Shutdown | IG01 | Internal shutdown | Feeder Shutdown taken for safety purpose
DJ Malpani - Palakkad | 2021-05-08 | Kerala | Palakkad | DJM06 | 2 | WTG | 5:38 | 6:11 | 0:33 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Attend turbine and check related connection than Start WTG
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM06 | 2 | WTG | 13:20 | 13:28 | 0:08 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-10 | Kerala | Palakkad | DJM06 | 2 | WTG | 12:46 | 12:54 | 0:08 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-12 | Kerala | Palakkad | DJM06 | 2 | WTG | 8:56 | 9:43 | 0:47 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-14 | Kerala | Palakkad | DJM06 | 2 | WTG | 13:19 | 13:31 | 0:12 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM06 | 2 | WTG | 14:58 | 15:06 | 0:08 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-16 | Kerala | Palakkad | DJM06 | 2 | WTG | 4:28 | 4:32 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-16 | Kerala | Palakkad | DJM06 | 2 | WTG | 18:20 | 18:24 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto Reset(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-04-01 | Kerala | Palakkad | DJM07 | 1 | WTG | 11:01 | 11:05 | 0:04 | Breakdown Maintenance | 23008 | Hub healthcheck timeout. | Auto Reset
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM07 | 1 | GA INT | 13:09 | 15:48 | 2:39 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-06 | Kerala | Palakkad | DJM07 | 1 | WTG | 4:58 | 5:06 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM07 | 1 | WTG | 4:35 | 4:43 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-11 | Kerala | Palakkad | DJM07 | 1 | WTG | 20:16 | 23:57 | 3:41 | Breakdown Maintenance | 7789 |  | Attend turbine check and found Generator slipring earthing carbon brush worn out after replace it than Start WTG
DJ Malpani - Palakkad | 2021-04-12 | Kerala | Palakkad | DJM07 | 1 | WTG | 7:49 | 7:53 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Auto Reset
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM07 | 1 | WTG | 3:00 | 3:16 | 0:16 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM07 | 1 | WTG | 6:56 | 7:04 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM07 | 1 | WTG | 20:35 | 20:39 | 0:04 | Breakdown Maintenance | 4135 | +CC100 temperature sensor is defective (Short cut or wire break). | Auto Reset
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM07 | 1 | GA INT | 16:43 | 17:59 | 1:16 | Feeder tripped E/F | IG02 | Earth Fault | Check and found B Phase Fuse open after Complate work resume both feeder
DJ Malpani - Palakkad | 2021-04-22 | Kerala | Palakkad | DJM07 | 1 | WTG | 13:28 | 13:32 | 0:04 | Breakdown Maintenance | 4135 | +CC100 temperature sensor is defective (Short cut or wire break). | Auto Reset
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM07 | 1 | WTG | 2:08 | 2:17 | 0:09 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM07 | 1 | WTG | 7:15 | 7:23 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-02 | Kerala | Palakkad | DJM07 | 1 | WTG | 3:57 | 4:01 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM07 | 1 | WTG | 6:11 | 6:15 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM07 | 1 | WTG | 6:20 | 6:24 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Auto Reset
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM07 | 1 | GA INT | 11:35 | 15:43 | 4:08 | Feeder tripped E/F | IG02 | Earth Fault | Check and found Y&B DO fuse failure and replaced ,then R,Y,B conductor replaced work complete after charge feeder
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM07 | 1 | WTG | 6:19 | 6:27 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-11 | Kerala | Palakkad | DJM07 | 1 | WTG | 12:59 | 13:03 | 0:04 | Breakdown Maintenance | 7768 | Stator voltage measurement fault. | WIP
DJ Malpani - Palakkad | 2021-05-14 | Kerala | Palakkad | DJM07 | 1 | WTG | 15:58 | 17:42 | 1:44 | Breakdown Maintenance | 10044 | Generator grounding brush worn error. | Replace grounding brush and Start WTG
DJ Malpani - Palakkad | 2021-05-14 | Kerala | Palakkad | DJM07 | 1 | WTG | 22:07 | 22:11 | 0:04 | Breakdown Maintenance | 30061 | Yaw converter is in state Error overload 2. | Auto Reset
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM07 | 1 | WTG | 14:36 | 14:59 | 0:23 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Reset and Start WTG(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-04-01 | Kerala | Palakkad | DJM08 | 2 | GA EXT | 20:04 | 20:25 | 0:21 | External Breakdown | EG02 | Grid Breakdown | Feeder tripped due to 220KV substation side Issue
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM08 | 2 | GA EXT | 1:22 | 4:31 | 3:09 | External Breakdown | EG02 | Grid Breakdown | Feeder tripped due to 220KV substation side Issue
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM08 | 2 | GA INT | 13:09 | 15:42 | 2:33 | Internal Shutdown | IG01 | Internal shutdown | Feeder Shutdown taken for safety purpose
DJ Malpani - Palakkad | 2021-04-03 | Kerala | Palakkad | DJM08 | 2 | WTG | 16:26 | 16:30 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-05 | Kerala | Palakkad | DJM08 | 2 | WTG | 23:55 | 23:59 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-06 | Kerala | Palakkad | DJM08 | 2 | WTG | 0:24 | 0:40 | 0:16 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM08 | 2 | WTG | 6:25 | 6:29 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-08 | Kerala | Palakkad | DJM08 | 2 | WTG | 3:26 | 3:30 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-10 | Kerala | Palakkad | DJM08 | 2 | WTG | 16:06 | 16:16 | 0:10 | Breakdown Maintenance | 31026 | Generator lubrication unit is in maintenance state. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-10 | Kerala | Palakkad | DJM08 | 2 | WTG | 18:19 | 18:23 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto Reset
DJ Malpani - Palakkad | 2021-04-11 | Kerala | Palakkad | DJM08 | 2 | WTG | 0:29 | 0:33 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-11 | Kerala | Palakkad | DJM08 | 2 | WTG | 5:03 | 5:07 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Auto Reset
DJ Malpani - Palakkad | 2021-04-12 | Kerala | Palakkad | DJM08 | 2 | WTG | 20:26 | 20:30 | 0:04 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-04-13 | Kerala | Palakkad | DJM08 | 2 | WTG | 21:36 | 21:40 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM08 | 2 | WTG | 2:58 | 3:14 | 0:16 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM08 | 2 | WTG | 4:20 | 4:24 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM08 | 2 | WTG | 6:41 | 6:49 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-16 | Kerala | Palakkad | DJM08 | 2 | WTG | 23:53 | 23:57 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM08 | 2 | WTG | 15:50 | 15:58 | 0:08 | Breakdown Maintenance | 31026 | Generator lubrication unit is in maintenance state. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM08 | 2 | GA INT | 16:54 | 17:59 | 1:05 | Internal Shutdown | IG01 | Internal shutdown | Feeder Shutdown taken for safety purpose
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM08 | 2 | WTG | 22:52 | 23:11 | 0:19 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-22 | Kerala | Palakkad | DJM08 | 2 | WTG | 6:19 | 6:35 | 0:16 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-23 | Kerala | Palakkad | DJM08 | 2 | WTG | 1:28 | 1:48 | 0:20 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-24 | Kerala | Palakkad | DJM08 | 2 | WTG | 4:53 | 5:01 | 0:08 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM08 | 2 | WTG | 3:27 | 3:31 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Auto Reset
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM08 | 2 | WTG | 7:13 | 7:23 | 0:10 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-25 | Kerala | Palakkad | DJM08 | 2 | WTG | 7:57 | 8:18 | 0:21 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-26 | Kerala | Palakkad | DJM08 | 2 | WTG | 1:48 | 1:57 | 0:09 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-26 | Kerala | Palakkad | DJM08 | 2 | WTG | 15:06 | 15:10 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto Reset
DJ Malpani - Palakkad | 2021-04-29 | Kerala | Palakkad | DJM08 | 2 | WTG | 1:57 | 2:07 | 0:10 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-30 | Kerala | Palakkad | DJM08 | 2 | WTG | 9:36 | 9:41 | 0:05 | Breakdown Maintenance | 31021 | Blade teeth lubrication is in maintenance state. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-30 | Kerala | Palakkad | DJM08 | 2 | WTG | 10:14 | 10:24 | 0:10 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-01 | Kerala | Palakkad | DJM08 | 2 | WTG | 23:03 | 23:11 | 0:08 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-03 | Kerala | Palakkad | DJM08 | 2 | WTG | 9:41 | 9:45 | 0:04 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-04 | Kerala | Palakkad | DJM08 | 2 | WTG | 22:43 | 22:47 | 0:04 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM08 | 2 | WTG | 6:48 | 7:00 | 0:12 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM08 | 2 | WTG | 9:42 | 9:46 | 0:04 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM08 | 2 | GA EXT | 21:36 | 22:01 | 0:25 | External Breakdown | EG02 | Grid Breakdown | Feeder tripped due to 220KV substation side Issue
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM08 | 2 | WTG | 22:01 | 22:21 | 0:20 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charge Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM08 | 2 | GA INT | 11:50 | 15:43 | 3:53 | Internal Shutdown | IG01 | Internal shutdown | Feeder Shutdown taken for safety purpose
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM08 | 2 | WTG | 15:57 | 16:01 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto Reset
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM08 | 2 | WTG | 20:10 | 20:32 | 0:22 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM08 | 2 | WTG | 6:21 | 6:25 | 0:04 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-10 | Kerala | Palakkad | DJM08 | 2 | WTG | 20:31 | 20:38 | 0:07 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-13 | Kerala | Palakkad | DJM08 | 2 | WTG | 20:37 | 20:45 | 0:08 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-14 | Kerala | Palakkad | DJM08 | 2 | WTG | 15:02 | 15:11 | 0:09 | Breakdown Maintenance | 31026 | Generator lubrication unit is in maintenance state. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM08 | 2 | WTG | 18:14 | 18:18 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Auto Reset(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-05-16 | Kerala | Palakkad | DJM08 | 2 | WTG | 10:00 | 10:04 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Auto Reset
DJ Malpani - Palakkad | 2021-05-17 | Kerala | Palakkad | DJM08 | 2 | WTG | 15:10 | 15:14 | 0:04 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-20 | Kerala | Palakkad | DJM08 | 2 | WTG | 15:11 | 16:39 | 1:28 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-01 | Kerala | Palakkad | DJM09 | 2 | GA EXT | 20:04 | 20:25 | 0:21 | External Breakdown | EG02 | Grid Breakdown | Feeder tripped due to 220KV substation side Issue
DJ Malpani - Palakkad | 2021-04-01 | Kerala | Palakkad | DJM09 | 2 | WTG | 21:23 | 21:41 | 0:18 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM09 | 2 | GA EXT | 1:22 | 4:31 | 3:09 | External Breakdown | EG02 | Grid Breakdown | Feeder tripped due to 220KV substation side Issue
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM09 | 2 | WTG | 9:50 | 10:56 | 1:06 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-02 | Kerala | Palakkad | DJM09 | 2 | GA INT | 13:09 | 15:42 | 2:33 | Internal Shutdown | IG01 | Internal shutdown | Feeder Shutdown taken for safety purpose
DJ Malpani - Palakkad | 2021-04-03 | Kerala | Palakkad | DJM09 | 2 | WTG | 16:27 | 16:36 | 0:09 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-04 | Kerala | Palakkad | DJM09 | 2 | WTG | 0:46 | 0:50 | 0:04 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM09 | 2 | WTG | 6:34 | 6:38 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-07 | Kerala | Palakkad | DJM09 | 2 | WTG | 9:23 | 9:35 | 0:12 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-10 | Kerala | Palakkad | DJM09 | 2 | WTG | 6:05 | 6:09 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-10 | Kerala | Palakkad | DJM09 | 2 | WTG | 8:14 | 8:53 | 0:39 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-11 | Kerala | Palakkad | DJM09 | 2 | WTG | 4:36 | 4:40 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-11 | Kerala | Palakkad | DJM09 | 2 | WTG | 7:29 | 7:35 | 0:06 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-12 | Kerala | Palakkad | DJM09 | 2 | WTG | 1:02 | 1:08 | 0:06 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-13 | Kerala | Palakkad | DJM09 | 2 | WTG | 18:47 | 19:21 | 0:34 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM09 | 2 | WTG | 0:06 | 0:14 | 0:08 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-14 | Kerala | Palakkad | DJM09 | 2 | WTG | 2:53 | 3:09 | 0:16 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM09 | 2 | WTG | 6:58 | 7:02 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-04-15 | Kerala | Palakkad | DJM09 | 2 | WTG | 14:07 | 14:19 | 0:12 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-16 | Kerala | Palakkad | DJM09 | 2 | WTG | 7:34 | 7:38 | 0:04 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM09 | 2 | GA INT | 16:54 | 17:59 | 1:05 | Internal Shutdown | IG01 | Internal shutdown | Feeder Shutdown taken for safety purpose
DJ Malpani - Palakkad | 2021-04-17 | Kerala | Palakkad | DJM09 | 2 | WTG | 20:44 | 20:56 | 0:12 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-22 | Kerala | Palakkad | DJM09 | 2 | WTG | 5:59 | 6:14 | 0:15 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-23 | Kerala | Palakkad | DJM09 | 2 | WTG | 18:07 | 18:19 | 0:12 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-26 | Kerala | Palakkad | DJM09 | 2 | WTG | 4:58 | 5:04 | 0:06 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-04-27 | Kerala | Palakkad | DJM09 | 2 | WTG | 19:55 | 20:29 | 0:34 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-28 | Kerala | Palakkad | DJM09 | 2 | WTG | 22:05 | 22:45 | 0:40 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-04-29 | Kerala | Palakkad | DJM09 | 2 | WTG | 16:01 | 16:35 | 0:34 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-01 | Kerala | Palakkad | DJM09 | 2 | WTG | 12:12 | 12:33 | 0:21 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-01 | Kerala | Palakkad | DJM09 | 2 | WTG | 23:22 | 23:30 | 0:08 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-02 | Kerala | Palakkad | DJM09 | 2 | WTG | 1:15 | 1:20 | 0:05 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-03 | Kerala | Palakkad | DJM09 | 2 | WTG | 20:33 | 20:57 | 0:24 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-03 | Kerala | Palakkad | DJM09 | 2 | WTG | 21:04 | 21:09 | 0:05 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM09 | 2 | WTG | 2:03 | 2:42 | 0:39 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-05 | Kerala | Palakkad | DJM09 | 2 | WTG | 6:54 | 7:02 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto Reset
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM09 | 2 | WTG | 15:54 | 16:25 | 0:31 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM09 | 2 | WTG | 16:25 | 16:37 | 0:12 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Auto Reset
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM09 | 2 | GA EXT | 21:36 | 22:01 | 0:25 | External Breakdown | EG02 | Grid Breakdown | Feeder tripped due to 220KV substation side Issue
DJ Malpani - Palakkad | 2021-05-06 | Kerala | Palakkad | DJM09 | 2 | WTG | 22:01 | 22:31 | 0:30 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charge Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM09 | 2 | GA INT | 11:50 | 15:43 | 3:53 | Internal Shutdown | IG01 | Internal shutdown | Feeder Shutdown taken for safety purpose
DJ Malpani - Palakkad | 2021-05-07 | Kerala | Palakkad | DJM09 | 2 | WTG | 16:17 | 16:23 | 0:06 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM09 | 2 | WTG | 8:30 | 8:44 | 0:14 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-09 | Kerala | Palakkad | DJM09 | 2 | WTG | 20:30 | 20:34 | 0:04 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Auto Reset
DJ Malpani - Palakkad | 2021-05-10 | Kerala | Palakkad | DJM09 | 2 | WTG | 13:39 | 13:45 | 0:06 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-11 | Kerala | Palakkad | DJM09 | 2 | WTG | 19:39 | 20:49 | 1:10 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Auto Reset
DJ Malpani - Palakkad | 2021-05-12 | Kerala | Palakkad | DJM09 | 2 | WTG | 3:12 | 6:58 | 3:46 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-13 | Kerala | Palakkad | DJM09 | 2 | WTG | 3:01 | 4:26 | 1:25 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-14 | Kerala | Palakkad | DJM09 | 2 | WTG | 7:28 | 8:50 | 1:22 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM09 | 2 | WTG | 2:08 | 3:33 | 1:25 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM09 | 2 | WTG | 11:00 | 17:16 | 6:16 | Breakdown Maintenance | SA17 | Special Activity - Repeated error rectification | Check related connection and Use 24v spare cable Nacelle tp OVP panel than Start WTG
DJ Malpani - Palakkad | 2021-05-15 | Kerala | Palakkad | DJM09 | 2 | WTG | 19:20 | 19:47 | 0:27 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset and Start WTG(Due to Grid Fluctuation)
DJ Malpani - Palakkad | 2021-05-16 | Kerala | Palakkad | DJM09 | 2 | WTG | 2:59 | 3:27 | 0:28 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-17 | Kerala | Palakkad | DJM09 | 2 | WTG | 4:16 | 4:28 | 0:12 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reset and Start WTG
DJ Malpani - Palakkad | 2021-05-18 | Kerala | Palakkad | DJM09 | 2 | WTG | 4:19 | 6:10 | 1:51 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-19 | Kerala | Palakkad | DJM09 | 2 | WTG | 11:55 | 14:52 | 2:57 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-20 | Kerala | Palakkad | DJM09 | 2 | WTG | 0:00 | 6:06 | 6:06 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot And Reset WTG
DJ Malpani - Palakkad | 2021-05-20 | Kerala | Palakkad | DJM09 | 2 | WTG | 9:44 | 23:59 | 14:15 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Checked CAN cable and related circuit WIP…
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT1 | 2 | GA INT | 11:59 | 14:34 | 2:35 | Internal Shutdown |  |  | FD-2 section isolator maintenance work and location no KKT 2 isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT1 | 2 | WTG | 11:33 | 19:53 | 8:20 | Preventive Maintenance |  |  | MS stop for USS yard isolater maintenance.
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT1 | 2 | WTG | 14:29 | 15:18 | 0:49 | Breakdown Maintenance |  |  | WTG MS due to OFC cable tighting work on 33kv pole so taken shutdown after tighting start WTG.
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT1 | 2 | GA INT | 10:40 | 12:51 | 2:11 | Internal Shutdown |  |  | FD-2 Shutdown taken due to safety purpose for work on F1
Giriraj Enterprises | 2021-04-22 | Madhya Pradesh | Kukru | KKT1 | 2 | WTG | 10:45 | 14:56 | 4:11 | Preventive Maintenance |  |  | WTG MS for USS YPM and ACB ,VCB testing work .
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT1 | 2 | GA INT | 15:13 | 16:12 | 0:59 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT10 | 1 | GA INT | 11:50 | 14:42 | 2:52 | Internal Shutdown |  |  | FD-1 section isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT10 | 1 | GA INT | 11:33 | 19:53 | 8:20 | Internal Shutdown |  |  | FD-1 Shutdown taken for USS yard isolater maintenance
Giriraj Enterprises | 2021-04-05 | Madhya Pradesh | Kukru | KKT10 | 1 | WTG | 10:16 | 15:31 | 5:15 | Preventive Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT10 | 1 | GA INT | 14:29 | 15:18 | 0:49 | Internal Shutdown |  |  | FD-1 Shutdown taken due to safety purpose for work on F2
Giriraj Enterprises | 2021-04-10 | Madhya Pradesh | Kukru | KKT10 | 1 | GA INT | 15:20 | 24:00 | 8:40 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT10 | 1 | GA INT | 0:00 | 15:15 | 15:15 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault then line petrolling found pole no. 132,112 pin insulator,KKT16 LA damaged and then replaced pin insulator and LA then charge feeder.
Giriraj Enterprises | 2021-04-13 | Madhya Pradesh | Kukru | KKT10 | 1 | FORCE MAJEURE | 14:07 | 23:59 | 9:52 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-14 | Madhya Pradesh | Kukru | KKT10 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-15 | Madhya Pradesh | Kukru | KKT10 | 1 | WTG | 0:00 | 10:56 | 10:56 | Breakdown Maintenance | 21006 | Safety chain - Overpower detected by SINEAX. | WTG stop due to Safety chain-Overpower detected by SINEAX. attend and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT10 | 1 | WTG | 15:42 | 20:40 | 4:58 | Breakdown Maintenance | 7044 | Converter LSA: Pole 3 hardware detected over current fault | WTG stop due to Convertor LSA: Pole 3 hardware detected over current fault attend and found 8 Amp HRC fuse burn after replacement WTG started.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT10 | 1 | GA INT | 14:56 | 15:58 | 1:02 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-05-19 | Madhya Pradesh | Kukru | KKT10 | 1 | WTG | 10:12 | 14:56 | 4:44 | Special Activity |  |  | WTG MS Structural Torquing and Tensioning work.
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 6:12 | 6:12 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT11 | 1 | GA INT | 11:50 | 14:42 | 2:52 | Internal Shutdown |  |  | FD-1 section isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT11 | 1 | GA INT | 11:33 | 19:53 | 8:20 | Internal Shutdown |  |  | FD-1 Shutdown taken for USS yard isolater maintenance
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 1:44 | 2:36 | 0:52 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT11 | 1 | GA INT | 14:29 | 15:18 | 0:49 | Internal Shutdown |  |  | FD-1 Shutdown taken due to safety purpose for work on F2
Giriraj Enterprises | 2021-04-08 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 3:17 | 4:34 | 1:17 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-08 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 18:02 | 19:50 | 1:48 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Encoder error persistence fault check all related connection then hard reboot and started.
Giriraj Enterprises | 2021-04-09 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 4:42 | 6:10 | 1:28 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high wind going on..
Giriraj Enterprises | 2021-04-09 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 10:56 | 16:15 | 5:19 | Breakdown Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-10 | Madhya Pradesh | Kukru | KKT11 | 1 | GA INT | 15:20 | 24:00 | 8:40 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT11 | 1 | GA INT | 0:00 | 15:15 | 15:15 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault then line petrolling found pole no. 132,112 pin insulator,KKT16 LA damaged and then replaced pin insulator and LA then charge feeder.
Giriraj Enterprises | 2021-04-13 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 13:03 | 23:59 | 10:56 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-14 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-15 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 20:20 | 20:20 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend and encoder tighted and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-17 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 1:22 | 10:04 | 8:42 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-18 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 2:11 | 3:07 | 0:56 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend and encoder tighted and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-18 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 20:48 | 21:58 | 1:10 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend an reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-20 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:53 | 7:40 | 6:47 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high wind going on
Giriraj Enterprises | 2021-04-21 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 4:39 | 4:39 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-22 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 5:32 | 5:32 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-23 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 21:52 | 22:43 | 0:51 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend an reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-24 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:39 | 10:49 | 10:10 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-25 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 1:42 | 4:42 | 3:00 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend an reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-26 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:41 | 4:18 | 3:37 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-27 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 3:29 | 9:32 | 6:03 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend and encoder tighted and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 2:31 | 9:28 | 6:57 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend and encoder tighted and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 13:03 | 14:35 | 1:32 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend and encoder tighted and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 15:09 | 15:54 | 0:45 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend and encoder tighted and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 23:00 | 23:59 | 0:59 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend and encoder tighted and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:52 | 1:18 | 0:26 | Breakdown Maintenance | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend and encoder tighted and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 2:24 | 4:41 | 2:17 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT11 | 1 | GA INT | 14:56 | 15:58 | 1:02 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-05-01 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 0:21 | 1:50 | 1:29 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-01 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 2:47 | 17:01 | 14:14 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-02 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:12 | 3:21 | 3:09 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-02 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 5:45 | 7:06 | 1:21 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-03 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 1:10 | 3:20 | 2:10 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-03 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 3:21 | 4:54 | 1:33 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-04 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 17:01 | 18:05 | 1:04 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-05 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:42 | 8:01 | 7:19 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-05 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 8:16 | 10:52 | 2:36 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-06 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 0:43 | 1:50 | 1:07 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-07 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 4:09 | 7:10 | 3:01 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-07 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 18:12 | 20:46 | 2:34 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-08 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 6:01 | 6:01 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-09 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:30 | 7:50 | 7:20 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-09 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 18:48 | 19:50 | 1:02 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-10 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 1:17 | 1:17 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-11 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 3:57 | 9:52 | 5:55 | Breakdown Maintenance |  |  | WTG MS for yaw motor replacement work .
Giriraj Enterprises | 2021-05-11 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 12:40 | 14:59 | 2:19 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-12 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:04 | 8:30 | 8:26 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-12 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 9:00 | 19:00 | 10:00 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-13 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 9:32 | 9:32 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-13 | Madhya Pradesh | Kukru | KKT11 | 1 | FORCE MAJEURE | 10:58 | 19:00 | 8:02 | COVID 19 | 7399 | Converter GSA: Encoder error persistence fault. | WTG stop due to Convertor GSA: Encodar error persistance fault . attend wtg and replace Generator encoder then started.
Giriraj Enterprises | 2021-05-14 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 2:08 | 5:56 | 3:48 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-14 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 14:49 | 16:21 | 1:32 | Breakdown Maintenance |  |  | WTG MS for blade Deraection preparation work.
Giriraj Enterprises | 2021-05-15 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 9:44 | 24:00 | 14:16 | Special Activity |  |  | WTG MS for blade de-erection for blade repair work.
Giriraj Enterprises | 2021-05-16 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Special Activity |  |  | WTG MS for blade de-erection for blade repair work.
Giriraj Enterprises | 2021-05-17 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Special Activity |  |  | WTG MS for blade de-erection for blade repair work.
Giriraj Enterprises | 2021-05-18 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Special Activity |  |  | WTG MS for blade de-erection for blade repair work.
Giriraj Enterprises | 2021-05-19 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Special Activity |  |  | WTG MS for blade de-erection for blade repair work.
Giriraj Enterprises | 2021-05-20 | Madhya Pradesh | Kukru | KKT11 | 1 | WTG | 0:00 | 24:00 | 24:00 | Special Activity |  |  | WTG MS for blade de-erection for blade repair work.
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT12 | 1 | GA INT | 11:50 | 14:42 | 2:52 | Internal Shutdown |  |  | FD-1 section isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT12 | 1 | GA INT | 11:33 | 19:53 | 8:20 | Internal Shutdown |  |  | FD-1 Shutdown taken for USS yard isolater maintenance
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT12 | 1 | GA INT | 14:29 | 15:18 | 0:49 | Internal Shutdown |  |  | FD-1 Shutdown taken due to safety purpose for work on F2
Giriraj Enterprises | 2021-04-10 | Madhya Pradesh | Kukru | KKT12 | 1 | WTG | 10:02 | 15:20 | 5:18 | Breakdown Maintenance |  |  | WTG MS due to gearbox box oil pump temperature raiset WIP.(due to feeder fault)
Giriraj Enterprises | 2021-04-10 | Madhya Pradesh | Kukru | KKT12 | 1 | GA INT | 15:20 | 24:00 | 8:40 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT12 | 1 | GA INT | 0:00 | 15:15 | 15:15 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault then line petrolling found pole no. 132,112 pin insulator,KKT16 LA damaged and then replaced pin insulator and LA then charge feeder.
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT12 | 1 | WTG | 15:15 | 18:49 | 3:34 | Breakdown Maintenance | 12026 | Hub grid fuse has opened. | WTG stop due to Hub grid fuse has oppened. Attend and check all hub fuses and connection ,pitch converter found pitch converter found all OK then start WTG.
Giriraj Enterprises | 2021-04-21 | Madhya Pradesh | Kukru | KKT12 | 1 | WTG | 10:32 | 15:08 | 4:36 | Preventive Maintenance |  |  | WTG MS for USS YPM and ACB ,VCB testing work .
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT12 | 1 | WTG | 12:53 | 13:48 | 0:55 | Breakdown Maintenance | 21006 | Safety chain - Overpower detected by SINEAX. | WTG stop due to Safety chain-Overpower detected by SINEAX. attend and reset & reboot then start WTG.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT12 | 1 | GA INT | 14:56 | 15:58 | 1:02 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-05-07 | Madhya Pradesh | Kukru | KKT12 | 1 | FORCE MAJEURE | 17:09 | 23:59 | 6:50 | COVID 19 | 11012 | Grid voltage is not OK. | WTG stop due to grid voltage is not ok . Unable to attend machine as facing pandemic condition due to COVID-19 WIP.
Giriraj Enterprises | 2021-05-08 | Madhya Pradesh | Kukru | KKT12 | 1 | FORCE MAJEURE | 0:00 | 9:39 | 9:39 | COVID 19 | 11012 | Grid voltage is not OK. | WTG stop due to grid voltage is not ok . Attend and check yard ACB found ACB burn tranformer megger value ok then start WTG. Unable to attend machine as facing pandemic condition due to COVID-19 WIP.
Giriraj Enterprises | 2021-05-15 | Madhya Pradesh | Kukru | KKT12 | 1 | WTG | 6:16 | 8:18 | 2:02 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | WTG stop due to Generator cooling water pressure low alarm. attend and top-up water coolent then start WTG.
Giriraj Enterprises | 2021-05-20 | Madhya Pradesh | Kukru | KKT12 | 1 | WTG | 6:30 | 11:00 | 4:30 | Breakdown Maintenance | 10044 | Generator grounding brush worn error. | WTG MS due generator grounding brush worn error attand and replace grounding brush then start wtg.
Giriraj Enterprises | 2021-05-20 | Madhya Pradesh | Kukru | KKT12 | 1 | WTG | 11:00 | 16:34 | 5:34 | Breakdown Maintenance |  |  | WTG MS Structural Torquing and Tensioning work.
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT13 | 2 | GA INT | 11:59 | 14:34 | 2:35 | Internal Shutdown |  |  | FD-2 section isolator maintenance work and location no KKT 2 isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT13 | 2 | WTG | 11:33 | 19:53 | 8:20 | Preventive Maintenance |  |  | MS stop for USS yard isolater maintenance.
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT13 | 2 | WTG | 14:29 | 15:18 | 0:49 | Breakdown Maintenance |  |  | WTG MS due to OFC cable tighting work on 33kv pole so taken shutdown after tighting start WTG.
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT13 | 2 | GA INT | 10:40 | 12:51 | 2:11 | Internal Shutdown |  |  | FD-2 Shutdown taken due to safety purpose for work on F1
Giriraj Enterprises | 2021-04-16 | Madhya Pradesh | Kukru | KKT13 | 2 | WTG | 11:19 | 16:19 | 5:00 | Breakdown Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT13 | 2 | WTG | 13:10 | 13:47 | 0:37 | Breakdown Maintenance |  |  | WTG stop due to HIGH wind.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT13 | 2 | GA INT | 15:13 | 16:12 | 0:59 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT14 | 2 | GA INT | 11:59 | 14:34 | 2:35 | Internal Shutdown |  |  | FD-2 section isolator maintenance work and location no KKT 2 isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT14 | 2 | WTG | 11:33 | 19:53 | 8:20 | Preventive Maintenance |  |  | MS stop for USS yard isolater maintenance.
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT14 | 2 | WTG | 14:29 | 15:18 | 0:49 | Breakdown Maintenance |  |  | WTG MS due to OFC cable tighting work on 33kv pole so taken shutdown after tighting start WTG.
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT14 | 2 | GA INT | 10:40 | 12:51 | 2:11 | Internal Shutdown |  |  | FD-2 Shutdown taken due to safety purpose for work on F1
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT14 | 2 | WTG | 21:05 | 22:30 | 1:25 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG stop due to Grid voltage is not ok .Attend found VCB tripped hold VCB then start WTG.
Giriraj Enterprises | 2021-04-18 | Madhya Pradesh | Kukru | KKT14 | 2 | WTG | 9:59 | 12:42 | 2:43 | Breakdown Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT14 | 2 | WTG | 13:47 | 14:20 | 0:33 | Breakdown Maintenance |  |  | WTG stop due to HIGH wind.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT14 | 2 | GA INT | 15:13 | 16:12 | 0:59 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-05-10 | Madhya Pradesh | Kukru | KKT14 | 2 | WTG | 14:07 | 16:30 | 2:23 | Breakdown Maintenance |  |  | WTG MS for yaw motor replacement work .
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 0:00 | 1:09 | 1:09 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT15 | 2 | GA INT | 11:59 | 14:34 | 2:35 | Internal Shutdown |  |  | FD-2 section isolator maintenance work and location no KKT 2 isolator maintenance work.
Giriraj Enterprises | 2021-04-02 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 10:47 | 16:15 | 5:28 | Preventive Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-02 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 16:15 | 19:49 | 3:34 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state. Attend and checked related connection then start WTG.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 11:33 | 19:53 | 8:20 | Preventive Maintenance |  |  | MS stop for USS yard isolater maintenance.
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 0:00 | 3:26 | 3:26 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 14:29 | 15:18 | 0:49 | Breakdown Maintenance |  |  | WTG MS due to OFC cable tighting work on 33kv pole so taken shutdown after tighting start WTG.
Giriraj Enterprises | 2021-04-08 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 0:00 | 2:39 | 2:39 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-08 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 23:29 | 23:59 | 0:30 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-09 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 0:05 | 5:12 | 5:07 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high wind going on..
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT15 | 2 | GA INT | 10:40 | 12:51 | 2:11 | Internal Shutdown |  |  | FD-2 Shutdown taken due to safety purpose for work on F1
Giriraj Enterprises | 2021-04-17 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 1:56 | 7:33 | 5:37 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-20 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 1:29 | 7:29 | 6:00 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high wind going on
Giriraj Enterprises | 2021-04-21 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 0:23 | 5:16 | 4:53 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-22 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 2:11 | 6:48 | 4:37 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-24 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 1:19 | 11:12 | 9:53 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-26 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 1:32 | 6:48 | 5:16 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-27 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 5:45 | 10:10 | 4:25 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 3:13 | 9:55 | 6:42 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 13:57 | 15:08 | 1:11 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 16:12 | 17:03 | 0:51 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 2:52 | 5:18 | 2:26 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT15 | 2 | GA INT | 15:13 | 16:12 | 0:59 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-05-01 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 3:12 | 13:55 | 10:43 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-02 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 0:05 | 3:21 | 3:16 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-05 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 3:30 | 6:52 | 3:22 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-07 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 6:38 | 7:46 | 1:08 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-08 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 3:06 | 6:22 | 3:16 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-11 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 4:39 | 9:42 | 5:03 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-12 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 0:10 | 9:00 | 8:50 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-13 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 0:10 | 10:25 | 10:15 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-14 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 2:41 | 6:32 | 3:51 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-17 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 6:48 | 10:27 | 3:39 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-18 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 11:26 | 16:50 | 5:24 | Special Activity |  |  | WTG MS Structural Torquing and Tensioning work.
Giriraj Enterprises | 2021-05-20 | Madhya Pradesh | Kukru | KKT15 | 2 | WTG | 13:40 | 14:15 | 0:35 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT16 | 1 | GA INT | 11:50 | 14:42 | 2:52 | Internal Shutdown |  |  | FD-1 section isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT16 | 1 | GA INT | 11:33 | 19:53 | 8:20 | Internal Shutdown |  |  | FD-1 Shutdown taken for USS yard isolater maintenance
Giriraj Enterprises | 2021-04-06 | Madhya Pradesh | Kukru | KKT16 | 1 | WTG | 2:32 | 11:00 | 8:28 | Breakdown Maintenance | 7529 | Converter system crowbar test failed. | WTG stop due to Convertor system crowbar test failed attend and found line contactor faulty breakdown continue due to material unavailibility.
Giriraj Enterprises | 2021-04-06 | Madhya Pradesh | Kukru | KKT16 | 1 | WTG | 11:00 | 15:00 | 4:00 | Preventive Maintenance |  |  | MS stop for USS yard isolater maintenance.
Giriraj Enterprises | 2021-04-06 | Madhya Pradesh | Kukru | KKT16 | 1 | WTG | 15:00 | 23:59 | 8:59 | Breakdown Maintenance | 7529 | Converter system crowbar test failed. | WTG stop due to Convertor system crowbar test failed attend and found line contactor faulty breakdown continue due to material unavailibility.
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT16 | 1 | WTG | 0:00 | 11:29 | 11:29 | Breakdown Maintenance | 7529 | Converter system crowbar test failed. | WTG stop due to Convertor system crowbar test failed attend and found line contactor faulty replaced line contracter and start WTG.
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT16 | 1 | GA INT | 14:29 | 15:18 | 0:49 | Internal Shutdown |  |  | FD-1 Shutdown taken due to safety purpose for work on F2
Giriraj Enterprises | 2021-04-10 | Madhya Pradesh | Kukru | KKT16 | 1 | GA INT | 15:20 | 24:00 | 8:40 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT16 | 1 | GA INT | 0:00 | 15:15 | 15:15 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault then line petrolling found pole no. 132,112 pin insulator,KKT16 LA damaged and then replaced pin insulator and LA then charge feeder.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT16 | 1 | GA INT | 14:56 | 15:58 | 1:02 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT19 | 2 | GA INT | 11:59 | 14:34 | 2:35 | Internal Shutdown |  |  | FD-2 section isolator maintenance work and location no KKT 2 isolator maintenance work.
Giriraj Enterprises | 2021-04-08 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 3:18 | 4:31 | 1:13 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-08 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 5:05 | 8:48 | 3:43 | Breakdown Maintenance | 5026 | Nacelle cabinet +3NCA200 fuse for external sensors is open/tripped. | WTG stop due to Nacelle cabinet +3NCA200 fuse for external sensors is open/tripped. Attend check related circuit and found fuse burn so after fuse replacement WTG started.
Giriraj Enterprises | 2021-04-09 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 1:25 | 3:18 | 1:53 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | WTG stop due to Deviation between active and demanded power is too high. Attend and found encoder lose and tight then start WTG.
Giriraj Enterprises | 2021-04-09 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 3:19 | 6:06 | 2:47 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high wind going on..
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT19 | 2 | GA INT | 10:40 | 12:51 | 2:11 | Internal Shutdown |  |  | FD-2 Shutdown taken due to safety purpose for work on F1
Giriraj Enterprises | 2021-04-14 | Madhya Pradesh | Kukru | KKT19 | 2 | FORCE MAJEURE | 20:58 | 23:59 | 3:01 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-15 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 0:00 | 11:06 | 11:06 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | WTG stop due to Generator cooling water pressure low alarm . Attend and coolent top up then start WTG.
Giriraj Enterprises | 2021-04-17 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 1:16 | 6:38 | 5:22 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-20 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 0:50 | 6:34 | 5:44 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high wind going on
Giriraj Enterprises | 2021-04-20 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 10:19 | 15:29 | 5:10 | Preventive Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-21 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 0:00 | 4:36 | 4:36 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-22 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 1:30 | 5:14 | 3:44 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-24 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 0:38 | 10:22 | 9:44 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-27 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 5:37 | 8:59 | 3:22 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 2:57 | 9:20 | 6:23 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 13:06 | 17:09 | 4:03 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 2:26 | 4:37 | 2:11 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT19 | 2 | GA INT | 15:13 | 16:12 | 0:59 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-05-01 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 2:43 | 10:38 | 7:55 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-02 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 0:01 | 4:17 | 4:16 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-04 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 11:02 | 12:13 | 1:11 | Breakdown Maintenance |  |  | WTG MS for USS ACB CT replacement work.
Giriraj Enterprises | 2021-05-07 | Madhya Pradesh | Kukru | KKT19 | 2 | FORCE MAJEURE | 5:27 | 9:36 | 4:09 | COVID 19 | 28006 | Generator cooling water pressure low alarm. | WTG stop due to Generator cooling water pressure low alarm . Attend and coolent top up then start WTG. Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-05-08 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 2:29 | 4:36 | 2:07 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-11 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 3:59 | 8:00 | 4:01 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-12 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 0:10 | 7:20 | 7:10 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-13 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 0:05 | 8:25 | 8:20 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-14 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 1:53 | 5:40 | 3:47 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-20 | Madhya Pradesh | Kukru | KKT19 | 2 | WTG | 7:38 | 9:16 | 1:38 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT2 | 2 | GA INT | 11:59 | 14:34 | 2:35 | Internal Shutdown |  |  | FD-2 section isolator maintenance work and location no KKT 2 isolator maintenance work.
Giriraj Enterprises | 2021-04-03 | Madhya Pradesh | Kukru | KKT2 | 2 | WTG | 13:58 | 15:08 | 1:10 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state. Attend and checked related connection then start WTG.
Giriraj Enterprises | 2021-04-05 | Madhya Pradesh | Kukru | KKT2 | 2 | WTG | 11:22 | 13:14 | 1:52 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state Attend and checked related connection UVR coil replaced then start WTG.
Giriraj Enterprises | 2021-04-06 | Madhya Pradesh | Kukru | KKT2 | 2 | WTG | 18:18 | 19:19 | 1:01 | Breakdown Maintenance | 7519 | Converter state was armed for too long time. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state Attend and checked related connection then start WTG.
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT2 | 2 | WTG | 14:29 | 15:18 | 0:49 | Breakdown Maintenance |  |  | WTG MS due to OFC cable tighting work on 33kv pole so taken shutdown after tighting start WTG.
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT2 | 2 | GA INT | 10:40 | 12:51 | 2:11 | Internal Shutdown |  |  | FD-2 Shutdown taken due to safety purpose for work on F1
Giriraj Enterprises | 2021-04-12 | Madhya Pradesh | Kukru | KKT2 | 2 | WTG | 9:30 | 14:52 | 5:22 | Preventive Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-13 | Madhya Pradesh | Kukru | KKT2 | 2 | FORCE MAJEURE | 0:18 | 2:04 | 1:46 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-13 | Madhya Pradesh | Kukru | KKT2 | 2 | FORCE MAJEURE | 15:47 | 23:59 | 8:12 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-14 | Madhya Pradesh | Kukru | KKT2 | 2 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-15 | Madhya Pradesh | Kukru | KKT2 | 2 | WTG | 0:00 | 11:02 | 11:02 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state Attend and checked related connection found ACB motor replaced then start WTG.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT2 | 2 | WTG | 13:20 | 14:13 | 0:53 | Breakdown Maintenance |  |  | WTG stop due to HIGH wind.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT2 | 2 | GA INT | 15:13 | 16:12 | 0:59 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 0:00 | 0:28 | 0:28 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT24 | 1 | GA INT | 11:50 | 14:42 | 2:52 | Internal Shutdown |  |  | FD-1 section isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT24 | 1 | GA INT | 11:33 | 19:53 | 8:20 | Internal Shutdown |  |  | FD-1 Shutdown taken for USS yard isolater maintenance
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT24 | 1 | GA INT | 14:29 | 15:18 | 0:49 | Internal Shutdown |  |  | FD-1 Shutdown taken due to safety purpose for work on F2
Giriraj Enterprises | 2021-04-08 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 9:47 | 16:20 | 6:33 | Preventive Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-10 | Madhya Pradesh | Kukru | KKT24 | 1 | GA INT | 15:20 | 24:00 | 8:40 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT24 | 1 | GA INT | 0:00 | 15:15 | 15:15 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault then line petrolling found pole no. 132,112 pin insulator,KKT16 LA damaged and then replaced pin insulator and LA then charge feeder.
Giriraj Enterprises | 2021-04-17 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 1:17 | 10:01 | 8:44 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high going on
Giriraj Enterprises | 2021-04-20 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 0:50 | 8:36 | 7:46 | Breakdown Maintenance |  |  | WTG MS due to blade crack and high wind going on
Giriraj Enterprises | 2021-04-21 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 0:00 | 4:36 | 4:36 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-22 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 1:31 | 6:07 | 4:36 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-24 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 0:39 | 10:23 | 9:44 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-27 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 5:38 | 9:50 | 4:12 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 3:49 | 9:20 | 5:31 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 13:17 | 15:08 | 1:51 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 2:23 | 4:40 | 2:17 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT24 | 1 | GA INT | 14:56 | 15:58 | 1:02 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-05-01 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 3:05 | 11:01 | 7:56 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-02 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 0:03 | 3:18 | 3:15 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-11 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 4:16 | 9:02 | 4:46 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-12 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 0:05 | 7:11 | 7:06 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-13 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 0:10 | 8:26 | 8:16 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-05-14 | Madhya Pradesh | Kukru | KKT24 | 1 | WTG | 2:04 | 5:51 | 3:47 | Breakdown Maintenance |  |  | WTG MS during high wind due to blade crack.
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT27 | 2 | GA INT | 11:59 | 14:34 | 2:35 | Internal Shutdown |  |  | FD-2 section isolator maintenance work and location no KKT 2 isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT27 | 2 | WTG | 11:33 | 19:53 | 8:20 | Preventive Maintenance |  |  | MS stop for USS yard isolater maintenance.
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT27 | 2 | WTG | 9:30 | 15:42 | 6:12 | Preventive Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT27 | 2 | WTG | 15:42 | 20:48 | 5:06 | Breakdown Maintenance | 7529 | Converter system crowbar test failed. | WTG stop due to Convertor system crowbar test failed attend and found line contactor faulty replaced line contracter and start WTG.
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT27 | 2 | GA INT | 10:40 | 12:51 | 2:11 | Internal Shutdown |  |  | FD-2 Shutdown taken due to safety purpose for work on F1
Giriraj Enterprises | 2021-04-14 | Madhya Pradesh | Kukru | KKT27 | 2 | FORCE MAJEURE | 15:32 | 23:59 | 8:27 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-15 | Madhya Pradesh | Kukru | KKT27 | 2 | WTG | 0:00 | 10:52 | 10:52 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | WTG stop due toTBC UPS module alarm. Attend and check all fuses and connection ,fuse fualty found found change fuse then start WTG.
Giriraj Enterprises | 2021-04-29 | Madhya Pradesh | Kukru | KKT27 | 2 | WTG | 13:08 | 14:14 | 1:06 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | WTG stop due to Grid voltage is not ok .Attend found VCB tripped hold VCB then start WTG.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT27 | 2 | GA INT | 15:13 | 16:12 | 0:59 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT7 | 1 | GA INT | 11:50 | 14:42 | 2:52 | Internal Shutdown |  |  | FD-1 section isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT7 | 1 | GA INT | 11:33 | 19:53 | 8:20 | Internal Shutdown |  |  | FD-1 Shutdown taken for USS yard isolater maintenance
Giriraj Enterprises | 2021-04-06 | Madhya Pradesh | Kukru | KKT7 | 1 | WTG | 15:56 | 16:19 | 0:23 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state Attend and replaced ACB charging motor then started.
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT7 | 1 | GA INT | 14:29 | 15:18 | 0:49 | Internal Shutdown |  |  | FD-1 Shutdown taken due to safety purpose for work on F2
Giriraj Enterprises | 2021-04-10 | Madhya Pradesh | Kukru | KKT7 | 1 | GA INT | 15:20 | 24:00 | 8:40 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT7 | 1 | GA INT | 0:00 | 15:15 | 15:15 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault then line petrolling found pole no. 132,112 pin insulator,KKT16 LA damaged and then replaced pin insulator and LA then charge feeder.
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT7 | 1 | WTG | 21:38 | 23:55 | 2:17 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state Attend and checked related connection found ACB motor replaced then start WTG.
Giriraj Enterprises | 2021-04-13 | Madhya Pradesh | Kukru | KKT7 | 1 | FORCE MAJEURE | 4:45 | 7:21 | 2:36 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-13 | Madhya Pradesh | Kukru | KKT7 | 1 | FORCE MAJEURE | 10:02 | 23:59 | 13:57 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-14 | Madhya Pradesh | Kukru | KKT7 | 1 | FORCE MAJEURE | 0:00 | 23:59 | 23:59 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-15 | Madhya Pradesh | Kukru | KKT7 | 1 | WTG | 0:00 | 20:10 | 20:10 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state Attend and checked related connection found ACB motor replaced then start WTG.
Giriraj Enterprises | 2021-04-16 | Madhya Pradesh | Kukru | KKT7 | 1 | WTG | 14:09 | 23:59 | 9:50 | Breakdown Maintenance | 7541 | GSC IGBT temperature above error limit. | WTG stop due to GSC IGBT temperture error limit.WIP.
Giriraj Enterprises | 2021-04-17 | Madhya Pradesh | Kukru | KKT7 | 1 | WTG | 0:00 | 16:18 | 16:18 | Breakdown Maintenance | 7541 | GSC IGBT temperature above error limit. | WTG stop due to GSC IGBT temperture error limit.attend and check PM3000 found PM3000 fualty & replaced PM3000 then start WTG.
Giriraj Enterprises | 2021-04-20 | Madhya Pradesh | Kukru | KKT7 | 1 | WTG | 12:55 | 18:40 | 5:45 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state Attend and checked related connection found ACB motor replaced then start WTG.
Giriraj Enterprises | 2021-04-25 | Madhya Pradesh | Kukru | KKT7 | 1 | WTG | 12:54 | 14:18 | 1:24 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | WTG stop due to stator breaker opened in production or didi not close in state synchronyzation state Attend and checked related connection found ACB motor supply connection loose after that tihgtened up connection then start WTG.
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT7 | 1 | GA INT | 14:56 | 15:58 | 1:02 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-05-01 | Madhya Pradesh | Kukru | KKT7 | 1 | FORCE MAJEURE | 14:10 | 17:15 | 3:05 | COVID 19 | 30007 | Each YCD shows internal errors. | WTG stop due to Each YCD shows internal errors. Unable to attend machine as facing pandemic condition due to COVID-19
Giriraj Enterprises | 2021-04-01 | Madhya Pradesh | Kukru | KKT9 | 1 | GA INT | 11:50 | 14:42 | 2:52 | Internal Shutdown |  |  | FD-1 section isolator maintenance work.
Giriraj Enterprises | 2021-04-04 | Madhya Pradesh | Kukru | KKT9 | 1 | GA INT | 11:33 | 19:53 | 8:20 | Internal Shutdown |  |  | FD-1 Shutdown taken for USS yard isolater maintenance
Giriraj Enterprises | 2021-04-07 | Madhya Pradesh | Kukru | KKT9 | 1 | GA INT | 14:29 | 15:18 | 0:49 | Internal Shutdown |  |  | FD-1 Shutdown taken due to safety purpose for work on F2
Giriraj Enterprises | 2021-04-10 | Madhya Pradesh | Kukru | KKT9 | 1 | GA INT | 15:20 | 24:00 | 8:40 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault
Giriraj Enterprises | 2021-04-11 | Madhya Pradesh | Kukru | KKT9 | 1 | GA INT | 0:00 | 15:15 | 15:15 | Internal Shutdown |  |  | FD-1 tripped on R pashe over current fault then line petrolling found pole no. 132,112 pin insulator,KKT16 LA damaged and then replaced pin insulator and LA then charge feeder.
Giriraj Enterprises | 2021-04-13 | Madhya Pradesh | Kukru | KKT9 | 1 | FORCE MAJEURE | 13:17 | 23:59 | 10:42 | ROW |  |  | WTG delay due to security gard & vehical vendar ROW.
Giriraj Enterprises | 2021-04-15 | Madhya Pradesh | Kukru | KKT9 | 1 | WTG | 0:00 | 23:51 | 23:51 | Breakdown Maintenance |  |  | WTG stop due to grid frequency from power measument device below operation range .Attend and check connection found VCB trip VCB charge and hold then start WTG.
Giriraj Enterprises | 2021-04-19 | Madhya Pradesh | Kukru | KKT9 | 1 | WTG | 10:43 | 18:51 | 8:08 | Preventive Maintenance |  |  | WTG MS for USS YPM and ACB VCB testing work .
Giriraj Enterprises | 2021-04-30 | Madhya Pradesh | Kukru | KKT9 | 1 | GA INT | 14:56 | 15:58 | 1:02 | Internal Shutdown |  |  | FD-1 tripped on R,Y pashe over current fault
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 5:01 | 6:17 | 1:16 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-04 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 5:46 | 6:35 | 0:49 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 15:34 | 15:38 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 7:00 | 7:10 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 7:44 | 7:52 | 0:08 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 17:38 | 17:44 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 18:16 | 18:24 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 8:48 | 9:05 | 0:17 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 15:03 | 15:15 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 15:48 | 15:56 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-15 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 18:59 | 19:03 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-15 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 19:05 | 19:09 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 21:57 | 22:01 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
Giriraj Enterprises | 2021-04-19 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 13:15 | 13:25 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-19 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 13:57 | 14:05 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 22:25 | 22:53 | 0:28 | Breakdown Maintenance | 6011 | TBC UPS module alarm. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 10:35 | 11:32 | 0:57 | Breakdown Maintenance |  |  | Manual reset and then start WTG.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 16:43 | 16:53 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 17:18 | 17:26 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and then start WTG.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 15:22 | 15:26 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 16:05 | 16:13 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 22:20 | 23:03 | 0:43 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 23:32 | 23:36 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 0:37 | 0:41 | 0:04 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 1:11 | 1:30 | 0:19 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 1:45 | 2:00 | 0:15 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 2:00 | 24:00 | 22:00 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | WIP.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 15:26 | 15:37 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 17:00 | 17:09 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 0:00 | 6:55 | 6:55 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | WIP.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 6:55 | 6:59 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 6:59 | 24:00 | 17:01 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | WIP.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | WIP.
Giriraj Enterprises | 2021-05-02 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | WIP. WTG unable to attend due to Vehicle ROW at site.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 0:00 | 17:12 | 17:12 | Covid 19 | 30009 | Maximum time for yaw positioning exceeded. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 17:12 | 17:16 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 17:16 | 24:00 | 6:44 | Covid 19 | 30009 | Maximum time for yaw positioning exceeded. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 0:00 | 4:25 | 4:25 | Covid 19 | 30009 | Maximum time for yaw positioning exceeded. | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 11:02 | 13:08 | 2:06 | Internal Shutdown | IG01 | Internal shutdown | LC taken by Inox for restoration of isolator work at MV2T38.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 13:41 | 13:53 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 17:58 | 18:03 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 18:35 | 18:43 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 16:15 | 16:22 | 0:07 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 16:56 | 17:04 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 15:54 | 16:07 | 0:13 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 17:48 | 17:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 15:19 | 15:35 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 15:35 | 24:00 | 8:25 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 0:00 | 7:42 | 7:42 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 7:42 | 11:30 | 3:48 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 11:30 | 24:00 | 12:30 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 0:00 | 4:40 | 4:40 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 4:40 | 4:50 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 4:50 | 19:50 | 15:00 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 19:50 | 20:25 | 0:35 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 20:25 | 24:00 | 3:35 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T1 | 3 | FORCE MAJEURE | 0:00 | 12:35 | 12:35 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG, delay due to facing pandemic condition Covid-19.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 15:44 | 15:50 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 16:51 | 16:56 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 17:28 | 17:36 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 18:31 | 18:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 19:14 | 19:22 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 15:13 | 15:17 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 15:31 | 15:59 | 0:28 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 16:28 | 17:38 | 1:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 19:54 | 20:17 | 0:23 | Breakdown Maintenance | 7140 | Converter GSA: Power Supply Fault 24V | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 8:33 | 8:41 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 18:28 | 18:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 18:54 | 19:28 | 0:34 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T1 | 3 | GA INT | 7:55 | 8:00 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T1 | 3 | WTG | 8:03 | 8:11 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-03 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 18:40 | 19:11 | 0:31 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Manual reset and start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 15:33 | 15:37 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 18:57 | 20:01 | 1:04 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 7:00 | 7:10 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 7:20 | 7:47 | 0:27 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Manual reset and start WTG.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 17:38 | 17:44 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 18:11 | 18:19 | 0:08 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 18:28 | 18:32 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 19:13 | 19:17 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 19:25 | 24:00 | 4:35 | Breakdown Maintenance | 28017 | Generator cooling slipring fan overload switch 1 is open/tripped. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 28017 | Generator cooling slipring fan overload switch 1 is open/tripped. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28017 | Generator cooling slipring fan overload switch 1 is open/tripped. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28017 | Generator cooling slipring fan overload switch 1 is open/tripped. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 0:00 | 15:03 | 15:03 | Breakdown Maintenance | 28017 | Generator cooling slipring fan overload switch 1 is open/tripped. | Torque limiter failure (delayed due to vehicle row).
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 15:03 | 15:15 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 15:15 | 24:00 | 8:45 | Breakdown Maintenance | 28017 | Generator cooling slipring fan overload switch 1 is open/tripped. | Torque limiter failure (delayed due to vehicle row).
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 0:00 | 17:50 | 17:50 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Replaced torque limiter and checked operation of ACB and start WTG.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 18:50 | 18:59 | 0:09 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 18:59 | 19:03 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-16 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 19:54 | 21:55 | 2:01 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Manual reset and start WTG.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 16:06 | 16:10 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 21:26 | 22:23 | 0:57 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Manual reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 10:00 | 12:19 | 2:19 | Preventive Maintenance |  |  | USS YPM work done.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 12:40 | 12:42 | 0:02 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 13:15 | 13:25 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 13:50 | 13:54 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-21 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 20:37 | 22:06 | 1:29 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Manual reset & then start WTG.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 21:40 | 22:00 | 0:20 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Auto reset.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 16:43 | 16:53 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 17:12 | 17:16 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 19:05 | 21:17 | 2:12 | Breakdown Maintenance | 1024 | Wind direction difference error. | Manual reset and then start WTG.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 15:18 | 15:22 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 12:17 | 14:18 | 2:01 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Manual reset and start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 14:18 | 14:46 | 0:28 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reboot PLC and manually reset, then start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 15:26 | 15:37 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 15:56 | 16:00 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 17:00 | 17:09 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 17:29 | 17:33 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 6:55 | 6:59 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 17:23 | 17:27 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
DJ Malpani | 2021-05-02 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 14:13 | 15:57 | 1:44 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Manual reset and start WTG.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 17:12 | 17:16 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 17:42 | 17:46 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 11:02 | 13:08 | 2:06 | Internal Shutdown | IG01 | Internal shutdown | LC taken by Inox for restoration of isolator work at MV2T38.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 13:19 | 13:23 | 0:04 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Auto reset.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 13:36 | 13:48 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 22:05 | 22:09 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 22:22 | 22:26 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 17:58 | 18:03 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 18:31 | 18:35 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 18:55 | 18:59 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 21:14 | 22:12 | 0:58 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 16:15 | 16:22 | 0:07 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 16:53 | 16:57 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 13:23 | 13:27 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 9:30 | 15:35 | 6:05 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Blade retrofitting work done.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 15:19 | 15:35 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 15:39 | 15:47 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after resume feeder.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 7:42 | 11:30 | 3:48 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 11:33 | 11:49 | 0:16 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after feeder resume.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 4:40 | 4:50 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 4:53 | 4:57 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 19:50 | 20:25 | 0:35 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T12 | 3 | FORCE MAJEURE | 20:42 | 24:00 | 3:18 | Covid 19 | 21006 | Safety chain - Overpower detected by SINEAX. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T12 | 3 | FORCE MAJEURE | 0:00 | 12:20 | 12:20 | Covid 19 | 21006 | Safety chain - Overpower detected by SINEAX. | Manual reset & then start WTG, delay due to facing pandemic condition Covid-19.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 12:20 | 15:10 | 2:50 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Blade retrofitting work done.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 15:44 | 15:50 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 16:51 | 16:56 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 16:59 | 17:03 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 9:26 | 18:31 | 9:05 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Released emergency switch, then reset and start WTG.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 18:31 | 18:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 18:40 | 23:03 | 4:23 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Released emergency switch, then reset and start WTG.
DJ Malpani | 2021-05-14 | Maharashtra | Vaspeth | MV2T12 | 3 | FORCE MAJEURE | 10:00 | 24:00 | 14:00 | Covid 19 | SA13 | Special Activity - Blade Retrofittment | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T12 | 3 | FORCE MAJEURE | 0:00 | 1:42 | 1:42 | Covid 19 | SA13 | Special Activity - Blade Retrofittment | Blade retrofitting work done.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 17:21 | 17:25 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 14:48 | 14:52 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 15:07 | 15:34 | 0:27 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 16:28 | 17:38 | 1:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 19:29 | 19:33 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 18:28 | 18:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 18:54 | 19:28 | 0:34 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T12 | 3 | WTG | 7:35 | 7:39 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T12 | 3 | GA INT | 7:55 | 8:00 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 3:02 | 3:18 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Tripped Due to E/F. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 3:48 | 4:02 | 0:14 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid resume.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 11:02 | 11:07 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 11:37 | 11:41 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-03 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 12:55 | 12:59 | 0:04 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Auto reset.
Giriraj Enterprises | 2021-04-03 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 16:59 | 17:02 | 0:03 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 13:46 | 13:50 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 15:06 | 15:11 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 15:36 | 15:40 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 19:07 | 19:12 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 19:28 | 19:37 | 0:09 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 22:07 | 22:37 | 0:30 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-08 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 3:35 | 3:43 | 0:08 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 9:50 | 9:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 10:20 | 10:24 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-10 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 16:15 | 16:19 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 3:39 | 4:28 | 0:49 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 4:28 | 4:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 5:04 | 5:08 | 0:04 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 14:05 | 14:09 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 2:06 | 2:17 | 0:11 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 4:06 | 4:22 | 0:16 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 8:18 | 8:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 14:19 | 14:25 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 14:54 | 14:58 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 15:31 | 15:35 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 15:52 | 18:12 | 2:20 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual rest & start WTG.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 16:39 | 16:43 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 16:48 | 16:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 17:18 | 17:22 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-15 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 10:27 | 10:31 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-15 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 15:00 | 17:50 | 2:50 | Preventive Maintenance |  |  | USS YPM work done.
Giriraj Enterprises | 2021-04-15 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 23:18 | 23:22 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 12:33 | 12:37 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 20:41 | 20:57 | 0:16 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Auto reset.
Giriraj Enterprises | 2021-04-16 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 23:05 | 23:31 | 0:26 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 4:40 | 4:47 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 4:47 | 4:51 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 5:17 | 5:21 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 11:38 | 11:42 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 15:43 | 15:48 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 15:48 | 15:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 16:18 | 16:22 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 18:50 | 18:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 18:55 | 18:59 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 19:26 | 19:30 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 19:42 | 21:15 | 1:33 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 12:27 | 12:31 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 14:00 | 20:25 | 6:25 | Internal Shutdown | IG01 | Internal shutdown | Line clearance taken by Inox. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 20:25 | 23:45 | 3:20 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
Giriraj Enterprises | 2021-04-19 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 16:30 | 16:34 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 11:09 | 11:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 11:59 | 12:11 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 22:00 | 22:20 | 0:20 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 6:20 | 6:30 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 6:59 | 7:03 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 8:58 | 9:02 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 13:08 | 13:12 | 0:04 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Auto reset.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 17:22 | 21:32 | 4:10 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Manual reset and then start WTG.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 12:23 | 12:39 | 0:16 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 13:43 | 13:47 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 16:04 | 23:38 | 7:34 | Breakdown Maintenance | 0 | Grid Loss | Checked and found observed VCB tripped, so after charge it, after start WTG.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 12:31 | 12:35 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 15:41 | 16:41 | 1:00 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 16:41 | 20:15 | 3:34 | Breakdown Maintenance | 0 | Grid Loss | Found yard VCB tripped condition charged yard VCB, then start WTG(Delay due to vehicle ROW and road bad condition due to heavy rain on site)
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 20:15 | 20:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 20:20 | 21:28 | 1:08 | Breakdown Maintenance | 0 | Grid Loss | Found yard VCB tripped condition charged yard VCB, then start WTG(Delay due to vehicle ROW and road bad condition due to heavy rain on site)
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 21:28 | 21:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 21:34 | 23:00 | 1:26 | Breakdown Maintenance | 0 | Grid Loss | Found yard VCB tripped condition charged yard VCB, then start WTG(Delay due to vehicle ROW and road bad condition due to heavy rain on site)
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 7:53 | 8:16 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 8:52 | 9:00 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 14:28 | 14:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 14:57 | 15:01 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 5:41 | 7:09 | 1:28 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 16:22 | 16:34 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 10:27 | 10:31 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 10:47 | 10:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 11:22 | 11:26 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 17:49 | 17:54 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 18:24 | 18:28 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 19:25 | 19:29 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 9:48 | 9:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 10:18 | 10:22 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 21:52 | 23:09 | 1:17 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Manual reset.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 14:18 | 14:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 14:53 | 14:57 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 18:26 | 18:34 | 0:08 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 11:08 | 11:12 | 0:04 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Auto reset.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 13:03 | 13:07 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 13:21 | 13:25 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 13:11 | 13:42 | 0:31 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 15:38 | 16:19 | 0:41 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T22 | 8 | FORCE MAJEURE | 16:07 | 19:20 | 3:13 | Covid 19 | 0 | Grid Loss | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 19:20 | 22:50 | 3:30 | Feeder tripped E/F | IG02 | Earth Fault | Tripped due to E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T22 | 8 | FORCE MAJEURE | 22:50 | 24:00 | 1:10 | Covid 19 | 0 | Grid Loss | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T22 | 8 | FORCE MAJEURE | 0:00 | 0:20 | 0:20 | Covid 19 | 0 | Grid Loss | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 12:45 | 14:23 | 1:38 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 14:57 | 15:09 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 18:35 | 24:00 | 5:25 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, trial not taken due to VCB Y pole stuck.WIP.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 0:00 | 14:18 | 14:18 | Feeder tripped O/C | IG03 | Over Current | Tripped by O/C, circuit breaker pole change, then checked & charged feeder ok.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 14:51 | 15:04 | 0:13 | Breakdown Maintenance | 31001 | Generator lubrication and yaw teeth lubrication overload switch failure. | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 13:13 | 13:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 13:48 | 13:52 | 0:04 | Breakdown Maintenance | 7009 | Converter LSA: Low line fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 18:38 | 18:42 | 0:04 | Breakdown Maintenance | 7516 | Stator breaker opened in production or did not close in state Synchronize GSC. | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 19:25 | 23:33 | 4:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 0:05 | 0:17 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 18:32 | 18:37 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 19:07 | 19:11 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 19:22 | 20:43 | 1:21 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 3:19 | 3:23 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 5:30 | 5:34 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 5:46 | 5:50 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 6:00 | 6:05 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 6:40 | 6:48 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 12:18 | 14:21 | 2:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 14:51 | 15:03 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 15:19 | 16:50 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 17:08 | 17:20 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 8:29 | 8:34 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 9:08 | 9:16 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 13:12 | 13:17 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 13:51 | 13:59 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 16:16 | 16:21 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 16:55 | 17:03 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 17:06 | 17:10 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 17:44 | 17:52 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 21:59 | 22:35 | 0:36 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 17:15 | 17:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 17:20 | 17:30 | 0:10 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after resume feeder.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 17:53 | 18:04 | 0:11 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after resume feeder.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 18:26 | 18:34 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 18:45 | 18:49 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 18:52 | 19:16 | 0:24 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-17 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 21:00 | 21:04 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 0:04 | 0:08 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 14:45 | 18:25 | 3:40 | Internal Shutdown | IG01 | Internal shutdown | Shutdown taken for tree cutting work.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 18:57 | 19:09 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 22:46 | 22:50 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 8:52 | 9:00 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T22 | 8 | GA INT | 8:13 | 8:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T22 | 8 | WTG | 8:22 | 8:30 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 3:02 | 3:18 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Tripped Due to E/F. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 3:20 | 3:43 | 0:23 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid resume.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 12:40 | 19:05 | 6:25 | Breakdown Maintenance | 28017 | Generator cooling slipring fan overload switch 1 is open/tripped. | Replaced with working slipring fan and start WTG.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 11:02 | 11:07 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 11:26 | 11:31 | 0:05 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 15:06 | 15:11 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 19:07 | 19:12 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 19:17 | 19:26 | 0:09 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 9:50 | 9:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 9:55 | 24:00 | 14:05 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-10 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 0:00 | 4:28 | 4:28 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 4:28 | 4:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 4:34 | 24:00 | 19:26 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 0:00 | 8:18 | 8:18 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 8:18 | 8:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 8:23 | 12:00 | 3:37 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 14:19 | 14:25 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 17:50 | 18:20 | 0:30 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 16:39 | 16:43 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 16:48 | 17:28 | 0:40 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-15 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 12:15 | 12:30 | 0:15 | Breakdown Maintenance | 0 | Grid Loss | Checked and found VCB tripped, checked for any abnormalities & start WTG.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 4:40 | 4:47 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 5:12 | 6:20 | 1:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 15:43 | 15:48 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 16:08 | 17:00 | 0:52 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 18:50 | 18:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 19:11 | 22:15 | 3:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG after grid.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 9:41 | 9:52 | 0:11 | Breakdown Maintenance | 0 | Grid Loss | Checked and found VCB tripped condition hence charged and start WTG.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 14:00 | 20:25 | 6:25 | Internal Shutdown | IG01 | Internal shutdown | Line clearance taken by Inox. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 20:25 | 23:22 | 2:57 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 11:09 | 11:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 11:30 | 18:20 | 6:50 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 6:17 | 6:20 | 0:03 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset then start WTG.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 6:20 | 6:30 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 6:30 | 10:16 | 3:46 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset then start WTG.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 16:53 | 22:49 | 5:56 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 15:41 | 16:41 | 1:00 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 16:41 | 24:00 | 7:19 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP, WTG unable to attend due to vehicle ROW and road bad condition due to heavy rain on site.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 20:15 | 20:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 21:28 | 21:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 0:00 | 7:53 | 7:53 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP, WTG unable to attend due to security ROW at site.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 7:53 | 8:16 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 8:16 | 14:28 | 6:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP, WTG unable to attend due to security ROW at site.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 14:28 | 14:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 14:33 | 24:00 | 9:27 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP, WTG unable to attend due to security ROW at site.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 0:00 | 15:21 | 15:21 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP, Unable to attend WTG due to vehicle ROW.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 4:48 | 4:52 | 0:04 | Breakdown Maintenance | 7513 | Converter state was precharge for too long time. | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 16:30 | 21:55 | 5:25 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 10:47 | 10:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 10:52 | 12:30 | 1:38 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset, delayed due to Vehicle ROW.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 17:49 | 17:54 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 17:54 | 24:00 | 6:06 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP. WTG unable to attend due to Vehicle ROW at site.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 0:00 | 13:25 | 13:25 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset delayed due to Vehicle ROW.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T27 | 8 | FORCE MAJEURE | 13:39 | 14:18 | 0:39 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 14:18 | 14:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T27 | 8 | FORCE MAJEURE | 14:23 | 17:48 | 3:25 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T27 | 8 | FORCE MAJEURE | 17:53 | 19:08 | 1:15 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T27 | 8 | FORCE MAJEURE | 14:45 | 23:10 | 8:25 | Covid 19 | 6010 | TBC 24VDC cabinet power supply is not OK. | Manual reset, delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 13:44 | 13:48 | 0:04 | Breakdown Maintenance | 7513 | Converter state was precharge for too long time. | Auto reset.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 15:38 | 16:19 | 0:41 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 17:28 | 19:06 | 1:38 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 19:20 | 22:50 | 3:30 | Feeder tripped E/F | IG02 | Earth Fault | Tripped due to E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 2:54 | 2:58 | 0:04 | Breakdown Maintenance | 4134 | CC101 24VDC buffer module for closing/opening breakers is not charged. | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T27 | 8 | FORCE MAJEURE | 8:22 | 11:56 | 3:34 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 12:45 | 14:23 | 1:38 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 12:58 | 13:06 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 14:07 | 14:11 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 18:35 | 24:00 | 5:25 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, trial not taken due to VCB Y pole stuck.WIP.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 0:00 | 14:18 | 14:18 | Feeder tripped O/C | IG03 | Over Current | Tripped by O/C, circuit breaker pole change, then checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 13:13 | 13:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 14:21 | 19:25 | 5:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 19:25 | 23:33 | 4:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T27 | 8 | FORCE MAJEURE | 23:33 | 24:00 | 0:27 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T27 | 8 | FORCE MAJEURE | 0:00 | 2:14 | 2:14 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG, delay due to facing pandemic condition Covid-19.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 18:32 | 18:37 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 18:37 | 18:41 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T27 | 8 | FORCE MAJEURE | 19:03 | 23:03 | 4:00 | Covid 19 | 21004 | Safety chain - Fuse opened. | PLC reboot,reset manually & restored WTG, delay due to facing pandemic condition Covid-19.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 6:00 | 6:05 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 12:18 | 14:21 | 2:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 15:19 | 16:50 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 16:50 | 18:30 | 1:40 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 7:09 | 9:56 | 2:47 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 8:29 | 8:34 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 13:12 | 13:17 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 16:16 | 16:21 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 17:06 | 17:10 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 21:24 | 21:28 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 17:15 | 17:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 17:53 | 19:25 | 1:32 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 0:04 | 0:08 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 12:50 | 13:42 | 0:52 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 14:45 | 18:25 | 3:40 | Internal Shutdown | IG01 | Internal shutdown | Shutdown taken for tree cutting work.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 18:57 | 19:09 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T27 | 8 | WTG | 22:46 | 22:50 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T27 | 8 | GA INT | 8:13 | 8:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 11:30 | 13:52 | 2:22 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 11:51 | 14:20 | 2:29 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-03 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:23 | 16:43 | 0:20 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-03 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:46 | 17:00 | 0:14 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-05 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 1:25 | 1:42 | 0:17 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot and reset,then start WTG.
DJ Malpani | 2021-04-05 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 1:50 | 2:20 | 0:30 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot and reset,then start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 1:25 | 1:42 | 0:17 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 13:53 | 14:30 | 0:37 | Preventive Maintenance |  |  | USS YPM work done.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 4:49 | 5:12 | 0:23 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Manual reset and start WTG.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 7:00 | 7:10 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 12:52 | 12:56 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 15:40 | 15:44 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 17:38 | 17:44 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 15:03 | 15:07 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 12:37 | 12:52 | 0:15 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset after grid.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 13:00 | 14:55 | 1:55 | Breakdown Maintenance | 0 | Grid Loss | Auto reset after grid.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 14:55 | 15:03 | 0:08 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset and start WTG.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 15:03 | 15:15 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 15:15 | 18:00 | 2:45 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset and start WTG.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 19:18 | 20:40 | 1:22 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG after grid.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 18:59 | 19:03 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-16 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 11:00 | 12:10 | 1:10 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 11:17 | 11:21 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 13:15 | 13:25 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 0:05 | 4:14 | 4:09 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and then start WTG.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 10:49 | 20:45 | 9:56 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 8:04 | 8:34 | 0:30 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 10:32 | 10:45 | 0:13 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 16:43 | 16:53 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:53 | 22:10 | 5:17 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and then start WTG.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 10:43 | 13:40 | 2:57 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:53 | 22:36 | 5:43 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 17:06 | 22:36 | 5:30 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 15:25 | 24:00 | 8:35 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | WIP, WTG unable to attend due to vehicle ROW and road bad condition due to heavy rain on site.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 0:00 | 6:58 | 6:58 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 12:10 | 12:14 | 0:04 | Breakdown Maintenance | 11015 | Fuse for power measurement device voltage measurement is open/broken. | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 0:00 | 7:44 | 7:44 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Charged VCB, after start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 10:55 | 14:46 | 3:51 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot PLC and manually reset, then start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 15:26 | 15:37 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 15:59 | 16:03 | 0:04 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:04 | 16:08 | 0:04 | Breakdown Maintenance | 11015 | Fuse for power measurement device voltage measurement is open/broken. | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:35 | 17:00 | 0:25 | Breakdown Maintenance | 22014 | Speed measurement generator speed below negative maximum. | Reboot PLC and manually reset, then start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 17:00 | 17:09 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 6:55 | 6:59 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 7:26 | 7:30 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 13:50 | 14:06 | 0:16 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot PLC and manually reset, then start WTG.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 14:19 | 14:34 | 0:15 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset & then start WTG.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:44 | 24:00 | 7:16 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | WIP. WTG unable to attend due to Vehicle ROW at site.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 0:00 | 12:58 | 12:58 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Reboot PLC and manually reset, then start WTG.
DJ Malpani | 2021-05-02 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 2:01 | 2:05 | 0:04 | Breakdown Maintenance | 7527 | Converter stator synchronization failed. | Auto reset.
DJ Malpani | 2021-05-02 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 2:55 | 24:00 | 21:05 | Breakdown Maintenance | 7238 | Converter GSA: Crowbar Triggerd Fault | WIP. WTG unable to attend due to Vehicle ROW at site.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T38 | 3 | FORCE MAJEURE | 2:55 | 17:12 | 14:17 | Covid 19 | 7238 | Converter GSA: Crowbar Triggerd Fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 17:12 | 17:16 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T38 | 3 | FORCE MAJEURE | 17:16 | 24:00 | 6:44 | Covid 19 | 7238 | Converter GSA: Crowbar Triggerd Fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T38 | 3 | FORCE MAJEURE | 0:00 | 11:02 | 11:02 | Covid 19 | 7238 | Converter GSA: Crowbar Triggerd Fault | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 11:02 | 13:08 | 2:06 | Internal Shutdown | IG01 | Internal shutdown | LC taken by Inox for restoration of isolator work at MV2T38.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T38 | 3 | FORCE MAJEURE | 13:08 | 13:10 | 0:02 | Covid 19 | 7238 | Converter GSA: Crowbar Triggerd Fault | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T38 | 3 | FORCE MAJEURE | 20:56 | 24:00 | 3:04 | Covid 19 | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T38 | 3 | FORCE MAJEURE | 0:00 | 0:40 | 0:40 | Covid 19 | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 17:58 | 18:03 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 18:31 | 18:35 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 10:03 | 11:42 | 1:39 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset & then start WTG.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 16:15 | 16:22 | 0:07 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:53 | 16:57 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:40 | 16:47 | 0:07 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 13:23 | 13:42 | 0:19 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset & then start WTG.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 18:15 | 18:30 | 0:15 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset & then start WTG.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 18:39 | 18:52 | 0:13 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset & then start WTG.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 10:03 | 11:42 | 1:39 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 15:19 | 15:35 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:53 | 16:57 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 7:42 | 11:30 | 3:48 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 8:33 | 8:45 | 0:12 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Auto reset.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 11:33 | 11:45 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after feeder resume.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 13:12 | 15:00 | 1:48 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset & then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:11 | 18:00 | 1:49 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset & then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 4:40 | 4:50 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 19:50 | 20:25 | 0:35 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 13:48 | 14:07 | 0:19 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 15:44 | 15:50 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 16:51 | 16:56 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 15:34 | 15:38 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 18:31 | 18:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 18:40 | 18:48 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after resume feeder.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 3:01 | 3:21 | 0:20 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 6:14 | 6:30 | 0:16 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 11:17 | 12:39 | 1:22 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | PLC reboot and reset then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 13:17 | 13:21 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 16:28 | 17:38 | 1:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 13:23 | 13:45 | 0:22 | Breakdown Maintenance | 21006 | Safety chain - Overpower detected by SINEAX. | Manual reset & then start WTG.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 12:15 | 12:40 | 0:25 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 14:02 | 14:18 | 0:16 | Breakdown Maintenance | 21006 | Safety chain - Overpower detected by SINEAX. | Manual reset & then start WTG.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 15:23 | 15:27 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T38 | 3 | WTG | 16:15 | 16:27 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charged WTG auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 18:28 | 18:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 18:54 | 19:28 | 0:34 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T38 | 3 | GA INT | 7:55 | 8:00 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 2:12 | 2:20 | 0:08 | Breakdown Maintenance | 31001 | Generator lubrication and yaw teeth lubrication overload switch failure. | Auto reset,after feeder resume WTG.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 3:02 | 3:18 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Tripped Due to E/F. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 13:46 | 15:28 | 1:42 | Breakdown Maintenance | 28019 | Generator cooling slipring fan overload switch 2 is open/tripped. | Checked related parameters not found any abnormalities, then tight the connection and reset and start WTG.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 9:54 | 10:02 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 11:02 | 11:07 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 11:07 | 11:11 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 13:50 | 13:54 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 15:06 | 15:11 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 17:47 | 17:55 | 0:08 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 19:07 | 19:12 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 7:57 | 8:01 | 0:04 | Breakdown Maintenance | 7140 | Converter GSA: Power Supply Fault 24V | Auto reset.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 10:41 | 10:45 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 12:27 | 12:31 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 8:31 | 8:39 | 0:08 | Breakdown Maintenance | 7529 | Converter system crowbar test failed. | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 8:41 | 8:45 | 0:04 | Breakdown Maintenance | 7529 | Converter system crowbar test failed. | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 8:47 | 8:51 | 0:04 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 8:53 | 9:50 | 0:57 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 9:50 | 9:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 9:55 | 24:00 | 14:05 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-10 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 0:00 | 4:28 | 4:28 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 4:28 | 4:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 4:34 | 24:00 | 19:26 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 0:00 | 8:18 | 8:18 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 8:18 | 8:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 8:23 | 11:38 | 3:15 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 11:43 | 11:51 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 12:38 | 12:45 | 0:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG after grid.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 14:19 | 14:25 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 13:59 | 14:07 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 16:39 | 16:43 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 16:48 | 16:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 4:40 | 4:47 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 5:15 | 5:23 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 15:43 | 15:48 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 16:12 | 16:21 | 0:09 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 18:50 | 18:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 19:16 | 19:24 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 14:00 | 20:25 | 6:25 | Internal Shutdown | IG01 | Internal shutdown | Line clearance taken by Inox. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 20:25 | 22:30 | 2:05 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
Giriraj Enterprises | 2021-04-19 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 15:55 | 15:59 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 11:09 | 11:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 6:12 | 6:20 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 6:20 | 6:30 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 8:07 | 8:15 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 10:01 | 10:08 | 0:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 15:13 | 15:25 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 14:46 | 14:58 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 15:41 | 16:41 | 1:00 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 16:41 | 16:43 | 0:02 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid resume , WTG auto reset.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 20:15 | 20:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 21:19 | 21:27 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid resume , WTG auto reset.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 21:28 | 21:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 21:59 | 22:07 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid resume , WTG auto reset.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 7:53 | 8:16 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 8:27 | 8:35 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 14:28 | 14:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 14:33 | 14:41 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 15:58 | 21:29 | 5:31 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 12:15 | 18:18 | 6:03 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 1:56 | 2:00 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 15:00 | 15:12 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 9:07 | 9:15 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 9:58 | 10:06 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 10:47 | 10:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 17:49 | 17:54 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 18:22 | 18:30 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 13:18 | 13:28 | 0:10 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-05-02 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 13:02 | 18:48 | 5:46 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset, delayed due to Vehicle ROW.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 14:18 | 14:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 14:49 | 14:57 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 18:14 | 18:22 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 14:49 | 14:57 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 15:38 | 16:19 | 0:41 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 16:19 | 16:25 | 0:06 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 18:41 | 18:53 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 19:16 | 19:20 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 19:20 | 22:50 | 3:30 | Feeder tripped E/F | IG02 | Earth Fault | Tripped due to E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 12:45 | 14:23 | 1:38 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T43 | 8 | FORCE MAJEURE | 14:23 | 23:15 | 8:52 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 4:57 | 5:01 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 7:59 | 8:01 | 0:02 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 18:35 | 24:00 | 5:25 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, trial not taken due to VCB Y pole stuck.WIP.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 0:00 | 14:18 | 14:18 | Feeder tripped O/C | IG03 | Over Current | Tripped by O/C, circuit breaker pole change, then checked & charged feeder ok.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 22:57 | 23:05 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 13:13 | 13:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 14:21 | 18:59 | 4:38 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 19:25 | 23:33 | 4:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 14:13 | 14:17 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 18:32 | 18:37 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 18:37 | 22:27 | 3:50 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 0:02 | 0:52 | 0:50 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 6:00 | 6:05 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 12:18 | 14:21 | 2:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 15:19 | 16:50 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 16:50 | 24:00 | 7:10 | Breakdown Maintenance |  |  | Checked and found auxiliary transformer input 440 contactor was burned, required 440V contactor, now WTG in stop condition.
Giriraj Enterprises | 2021-05-14 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 0:00 | 2:06 | 2:06 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | PLC reboot & reset WTG.
Giriraj Enterprises | 2021-05-14 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 18:54 | 20:23 | 1:29 | Breakdown Maintenance | 0 | Grid Loss | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-14 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 23:30 | 24:00 | 0:30 | Breakdown Maintenance | 0 | Grid Loss | WIP.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 0:00 | 0:46 | 0:46 | Breakdown Maintenance | 0 | Grid Loss | VCB charged and start WTG.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 8:29 | 8:34 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 8:34 | 11:02 | 2:28 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 13:12 | 13:17 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 16:16 | 16:21 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 17:06 | 17:10 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 17:10 | 24:00 | 6:50 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to access location due to bad road condition.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 0:00 | 1:10 | 1:10 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Checked and found VCB tripped, so checked related paramters, then charged VCB, then start WTG.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T43 | 8 | FORCE MAJEURE | 12:24 | 17:15 | 4:51 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | PLC reboot,reset manually & restored WTG, delay due to facing pandemic condition Covid-19.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 17:15 | 17:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 17:20 | 17:48 | 0:28 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 17:53 | 18:57 | 1:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 14:45 | 18:25 | 3:40 | Internal Shutdown | IG01 | Internal shutdown | Shutdown taken for tree cutting work.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T43 | 8 | WTG | 18:25 | 19:20 | 0:55 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid resume, WTG manual reset.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T43 | 8 | GA INT | 8:13 | 8:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:44 | 12:48 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:50 | 12:54 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:56 | 13:00 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:01 | 13:11 | 0:10 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:22 | 13:25 | 0:03 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:11 | 14:15 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:20 | 14:39 | 0:19 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:48 | 14:54 | 0:06 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:54 | 14:55 | 0:01 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:58 | 15:02 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 20:07 | 20:11 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 20:11 | 20:41 | 0:30 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Manual reset and start WTG.
DJ Malpani | 2021-04-02 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:34 | 17:54 | 1:20 | Breakdown Maintenance | 31021 | Blade teeth lubrication is in maintenance state. | Manual reset and start WTG.
DJ Malpani | 2021-04-03 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:45 | 11:49 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-03 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:27 | 12:31 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-05 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:54 | 18:02 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-05 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 22:28 | 22:32 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 1:10 | 1:14 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 1:18 | 1:28 | 0:10 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Manual reset and start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 1:32 | 1:36 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:45 | 18:49 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:53 | 19:25 | 0:32 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Manual reset and start WTG.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 7:00 | 7:10 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 7:10 | 7:22 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:42 | 11:46 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:49 | 11:53 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:53 | 13:07 | 1:14 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:08 | 13:12 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:14 | 13:18 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:19 | 13:58 | 0:39 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:19 | 14:23 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:26 | 14:30 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:32 | 14:45 | 0:13 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG>
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:39 | 16:43 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:55 | 16:59 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:34 | 17:38 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:00 | 15:25 | 2:25 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
DJ Malpani | 2021-04-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:38 | 15:42 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:01 | 16:05 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:25 | 16:26 | 0:01 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:26 | 16:27 | 0:01 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:29 | 16:33 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 8:09 | 8:13 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:02 | 15:06 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:24 | 17:28 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 17:38 | 17:44 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:44 | 17:46 | 0:02 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:55 | 17:59 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:14 | 18:18 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:54 | 20:40 | 0:46 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset and start WTG.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 20:42 | 21:05 | 0:23 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:03 | 0:07 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 3:41 | 3:45 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 3:45 | 3:49 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 3:50 | 3:54 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 4:04 | 5:01 | 0:57 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 5:02 | 5:06 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 5:11 | 5:15 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 6:29 | 6:40 | 0:11 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 6:42 | 6:46 | 0:04 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:33 | 13:37 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:44 | 13:48 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:51 | 14:49 | 0:58 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:26 | 16:30 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:08 | 16:12 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:18 | 17:22 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:52 | 19:50 | 0:58 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset and start WTG.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 22:17 | 22:21 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 3:31 | 3:35 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 4:19 | 4:23 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 4:49 | 6:49 | 2:00 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 7:01 | 7:05 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 8:18 | 8:27 | 0:09 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 9:02 | 9:06 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:52 | 12:58 | 0:06 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:28 | 13:32 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:34 | 13:38 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:00 | 24:00 | 7:00 | Breakdown Maintenance | 7139 | Converter GSA: DC-Bus Hardware Overvoltage Fault | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:00 | 15:08 | 15:08 | Breakdown Maintenance | 7139 | Converter GSA: DC-Bus Hardware Overvoltage Fault | Delayed due to vehicle Row. Manual reset and start WTG.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 15:03 | 15:15 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:26 | 15:44 | 0:18 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:22 | 19:26 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:37 | 19:41 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 6:03 | 6:05 | 0:02 | Breakdown Maintenance | 28006 | Generator cooling water pressure low alarm. | Manual reset and start WTG.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 7:09 | 9:34 | 2:25 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG (error due to low wind)
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:20 | 15:24 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:30 | 15:38 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:46 | 17:59 | 2:13 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & start WTG.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:29 | 19:33 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:31 | 14:08 | 1:37 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG(error due to low wind)
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:30 | 18:34 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 18:59 | 19:03 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 3:26 | 3:39 | 0:13 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG(error due to low wind).
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:48 | 16:55 | 0:07 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG(error due to low wind).
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 2:45 | 2:49 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 3:08 | 3:12 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 3:17 | 3:29 | 0:12 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 22:39 | 22:43 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 22:54 | 22:58 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 23:22 | 23:26 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 23:34 | 24:00 | 0:26 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | WIP.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:00 | 2:33 | 2:33 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 13:15 | 13:25 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:26 | 13:34 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:43 | 14:47 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:47 | 17:59 | 1:12 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:00 | 18:04 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:27 | 13:31 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:35 | 14:14 | 0:39 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:04 | 16:08 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:08 | 16:12 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:24 | 16:36 | 0:12 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:45 | 17:01 | 0:16 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 4:01 | 4:05 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG could not attend due to vehicle ROW.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 4:07 | 4:11 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG could not attend due to vehicle ROW.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:34 | 15:38 | 2:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | WTG could not attend due to vehicle ROW.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 2:36 | 6:33 | 3:57 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 8:15 | 8:19 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:16 | 15:17 | 3:01 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:17 | 15:30 | 0:13 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:30 | 16:43 | 1:13 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 16:43 | 16:53 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:53 | 17:06 | 0:13 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:06 | 17:33 | 0:27 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:33 | 21:50 | 4:17 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and then start WTG.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 9:27 | 9:31 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 9:32 | 11:28 | 1:56 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | PLC reboot and reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:38 | 11:53 | 0:15 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:39 | 14:43 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:05 | 16:13 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 21:06 | 21:59 | 0:53 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 23:14 | 23:18 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 10:58 | 13:38 | 2:40 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Manual reset and start WTG.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:35 | 15:43 | 0:08 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset and start WTG.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:54 | 15:58 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:44 | 16:48 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:02 | 17:07 | 0:05 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:07 | 17:17 | 0:10 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 20:44 | 20:48 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 20:51 | 20:55 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 20:59 | 21:03 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 21:07 | 22:50 | 1:43 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset and start WTG.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 8:29 | 21:23 | 12:54 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset and start WTG.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 22:03 | 24:00 | 1:57 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | WIP, WTG unable to attend due to security ROW at site.
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:00 | 11:43 | 11:43 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset and start WTG.
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:52 | 11:56 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:04 | 17:32 | 5:28 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:01 | 22:09 | 3:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset and start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:52 | 11:56 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:04 | 17:07 | 5:03 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 15:26 | 15:37 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 17:00 | 17:09 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:01 | 22:14 | 3:13 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:00 | 5:37 | 5:37 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | VCB Found tripped charge the VCB and start the WTG.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 6:55 | 6:59 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 6:59 | 7:12 | 0:13 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 7:42 | 11:13 | 3:31 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:22 | 11:47 | 0:25 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:00 | 24:00 | 12:00 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Due to low wind error repeats.WIP.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:00 | 13:39 | 13:39 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset delayed due to Vehicle ROW.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:31 | 18:24 | 4:53 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset delayed due to Vehicle ROW.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 20:05 | 20:09 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-02 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 8:13 | 12:21 | 4:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset, delayed due to Vehicle ROW.
DJ Malpani | 2021-05-02 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:19 | 18:52 | 5:33 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset, delayed due to Vehicle ROW.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 12:09 | 15:01 | 2:52 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 17:12 | 17:16 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:16 | 17:19 | 0:03 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 17:55 | 19:25 | 1:30 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 11:02 | 13:08 | 2:06 | Internal Shutdown | IG01 | Internal shutdown | LC taken by Inox for restoration of isolator work at MV2T38.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:09 | 13:21 | 0:12 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 13:22 | 15:18 | 1:56 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 21:54 | 21:58 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 23:14 | 24:00 | 0:46 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 0:00 | 11:13 | 11:13 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:39 | 17:43 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 17:58 | 18:03 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:03 | 18:11 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 9:41 | 9:45 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:22 | 15:23 | 1:01 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 16:15 | 16:22 | 0:07 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:33 | 18:35 | 0:02 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:37 | 18:41 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:45 | 18:49 | 0:04 | Breakdown Maintenance | 23009 | Hub healthcheck alarm. | Auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 23:21 | 23:24 | 0:03 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 23:29 | 23:43 | 0:14 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 6:40 | 15:38 | 8:58 | Covid 19 | 28006 | Generator cooling water pressure low alarm. | Manual reset, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:17 | 17:28 | 0:11 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 17:56 | 24:00 | 6:04 | Covid 19 | 28006 | Generator cooling water pressure low alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 0:00 | 3:00 | 3:00 | Covid 19 | 28006 | Generator cooling water pressure low alarm. | Coolant top up work done and start WTG.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 4:57 | 5:01 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 7:59 | 8:01 | 0:02 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 9:58 | 10:53 | 0:55 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:56 | 14:05 | 0:09 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:26 | 14:30 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:46 | 15:30 | 0:44 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:55 | 15:59 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:45 | 23:50 | 6:05 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:03 | 0:07 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:16 | 0:20 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:20 | 1:16 | 0:56 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Reboot PLC and reset WTG.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:04 | 11:08 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:09 | 11:13 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:13 | 11:21 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:21 | 11:45 | 0:24 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:46 | 12:28 | 0:42 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:38 | 12:47 | 0:09 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:46 | 15:19 | 0:33 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 15:19 | 15:35 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 15:35 | 24:00 | 8:25 | Covid 19 | 0 | Grid Loss | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 0:00 | 7:42 | 7:42 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Checked and found VCB tripped, so checked related parameters not found any abnormalities, so charged VCB, then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 7:42 | 11:30 | 3:48 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 11:30 | 12:49 | 1:19 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Checked and found VCB tripped, so checked related parameters not found any abnormalities, so charged VCB, then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:50 | 13:55 | 1:05 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:56 | 15:39 | 1:43 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:40 | 15:44 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:46 | 15:50 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:58 | 17:46 | 0:48 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:47 | 18:02 | 0:15 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:05 | 19:09 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:09 | 19:13 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:15 | 22:16 | 3:01 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 4:40 | 4:50 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 4:50 | 4:57 | 0:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:43 | 15:20 | 2:37 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 19:14 | 19:18 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 19:50 | 20:25 | 0:35 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 20:25 | 24:00 | 3:35 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T44 | 3 | FORCE MAJEURE | 0:00 | 12:30 | 12:30 | Covid 19 | 0 | Grid Loss | PLC reboot,reset manually & restored WTG, delay due to facing pandemic condition Covid-19.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 12:47 | 13:57 | 1:10 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:47 | 14:56 | 0:09 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:11 | 15:44 | 0:33 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 15:44 | 15:50 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:50 | 16:47 | 0:57 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 16:51 | 16:56 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:56 | 17:04 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:10 | 14:14 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:17 | 14:21 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:35 | 14:52 | 0:17 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:15 | 16:19 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:24 | 16:28 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:44 | 17:36 | 0:52 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 18:31 | 18:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:40 | 22:44 | 4:04 | Breakdown Maintenance | 0 | Grid Loss | We checked and found VCB tripped, so checked related parameters not found any abnormalities, so charged VCB, then start WTG..
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 22:44 | 22:48 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-14 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:03 | 11:07 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-14 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:25 | 15:32 | 4:07 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 14:50 | 14:54 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:02 | 15:06 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 16:01 | 17:07 | 1:06 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset & then start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:58 | 18:02 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:06 | 18:10 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:13 | 24:00 | 5:47 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Unable to access location due to bad road condition.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 0:00 | 3:47 | 3:47 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Checked and found VCB tripped, so checked related paramters, then charged VCB, then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:00 | 13:02 | 0:02 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:25 | 13:29 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:33 | 13:37 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 13:41 | 15:26 | 1:45 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:38 | 15:42 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:46 | 15:50 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 15:54 | 16:28 | 0:34 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 16:28 | 17:38 | 1:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 17:38 | 18:09 | 0:31 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:24 | 22:02 | 3:38 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 22:13 | 22:17 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 22:45 | 22:57 | 0:12 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset & then start WTG.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 8:52 | 8:56 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 10:31 | 10:35 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:29 | 11:31 | 0:02 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 11:47 | 11:51 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-18 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 8:46 | 8:50 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 8:01 | 8:09 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 18:28 | 18:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 18:34 | 18:38 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charged manual reset & start WTG.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 18:54 | 19:28 | 0:34 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T44 | 3 | GA INT | 7:55 | 8:00 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 8:01 | 8:09 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T44 | 3 | WTG | 20:04 | 22:27 | 2:23 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 2:38 | 2:42 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset.
DJ Malpani | 2021-04-03 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 10:44 | 10:48 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-05 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 18:44 | 19:25 | 0:41 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Manual reset and start WTG.
DJ Malpani | 2021-04-05 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 19:38 | 24:00 | 4:22 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | WIP.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:00 | 5:10 | 5:10 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Checked related circuit and 2 yaw motors hardware damage, so replaced and yaw brake gap set, then start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 11:13 | 11:17 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 14:41 | 14:45 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 6:42 | 6:50 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 7:00 | 7:10 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 16:39 | 16:43 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:58 | 14:02 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 17:09 | 17:17 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 17:38 | 17:44 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:09 | 13:13 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:47 | 15:51 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 7:47 | 7:55 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 12:28 | 12:32 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:35 | 14:39 | 1:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 15:03 | 15:15 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 23:48 | 24:00 | 0:12 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | Auto reset.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 1:54 | 2:32 | 0:38 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 2:45 | 3:30 | 0:45 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | Checked all cooling fan working ok, reduced temperature by external wind and start WTG.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 17:46 | 17:54 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 18:59 | 19:03 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-16 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:37 | 13:41 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 13:15 | 13:25 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:25 | 14:45 | 1:20 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:41 | 15:45 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 2:46 | 16:50 | 14:04 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | Yaw twist setting done and cable twist remove, then start the WTG.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 21:59 | 24:00 | 2:01 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | Yaw twist setting done and cable twist remove, then start the WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:00 | 4:00 | 4:00 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | Yaw twist setting done and cable twist remove, then start the WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:17 | 15:30 | 0:13 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and then start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 16:43 | 16:53 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 16:53 | 23:02 | 6:09 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and then start WTG.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 12:16 | 12:41 | 0:25 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:39 | 15:43 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 16:04 | 24:00 | 7:56 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:00 | 0:26 | 0:26 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | PLC reboot and reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:17 | 15:21 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:41 | 16:22 | 0:41 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Manual reset and start WTG.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 17:02 | 24:00 | 6:58 | Breakdown Maintenance | 28019 | Generator cooling slipring fan overload switch 2 is open/tripped. | WIP, WTG unable to attend due to vehicle ROW and road bad condition due to heavy rain on site.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28019 | Generator cooling slipring fan overload switch 2 is open/tripped. | WIP, WTG unable to attend due to security ROW at site.
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 28019 | Generator cooling slipring fan overload switch 2 is open/tripped. | WIP, Unable to attend WTG due to vehicle ROW.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:00 | 6:45 | 6:45 | Breakdown Maintenance | 28019 | Generator cooling slipring fan overload switch 2 is open/tripped. | Replace generator cooling slipring fan after start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:27 | 13:31 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:31 | 13:35 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 14:26 | 15:26 | 1:00 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | WIP.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 15:26 | 15:37 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:37 | 17:00 | 1:23 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | WIP.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 17:00 | 17:09 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 17:09 | 24:00 | 6:51 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | WIP.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:00 | 6:55 | 6:55 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | WIP.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 6:55 | 6:59 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 6:59 | 24:00 | 17:01 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | WIP.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | WIP.
DJ Malpani | 2021-05-02 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | WIP. WTG unable to attend due to Vehicle ROW at site.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 0:00 | 17:12 | 17:12 | Covid 19 | 30063 | Yaw converter is in state Error external fault. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 17:12 | 17:16 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 17:16 | 24:00 | 6:44 | Covid 19 | 30063 | Yaw converter is in state Error external fault. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 0:00 | 5:44 | 5:44 | Covid 19 | 30063 | Yaw converter is in state Error external fault. | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 11:02 | 13:08 | 2:06 | Internal Shutdown | IG01 | Internal shutdown | LC taken by Inox for restoration of isolator work at MV2T38.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 11:04 | 11:16 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:19 | 13:23 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 22:22 | 22:26 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 11:08 | 11:12 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 17:58 | 18:03 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 18:30 | 18:38 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 14:20 | 15:50 | 1:30 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Manual reset & then start WTG.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 16:15 | 16:22 | 0:07 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 16:38 | 16:46 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:46 | 15:50 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 17:31 | 17:42 | 0:11 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 14:08 | 14:12 | 0:04 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 14:31 | 14:35 | 0:04 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:21 | 13:32 | 0:11 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & then start WTG.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 15:19 | 15:35 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 15:35 | 24:00 | 8:25 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 0:00 | 7:42 | 7:42 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 7:42 | 11:30 | 3:48 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 11:30 | 12:42 | 1:12 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 1:07 | 1:15 | 0:08 | Breakdown Maintenance | 7009 | Converter LSA: Low line fault | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 4:40 | 4:50 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 7:13 | 7:17 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 9:42 | 9:46 | 0:04 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 10:11 | 10:14 | 0:03 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:56 | 14:15 | 0:19 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 15:28 | 19:50 | 4:22 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 19:50 | 20:25 | 0:35 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 20:25 | 24:00 | 3:35 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 0:00 | 0:05 | 0:05 | Covid 19 | 21004 | Safety chain - Fuse opened. | PLC reboot,reset manually & restored WTG, delay due to facing pandemic condition Covid-19.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 3:20 | 15:44 | 12:24 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | Manual reset & then start WTG, delay due to facing pandemic condition Covid-19.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 15:44 | 15:50 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 15:50 | 16:51 | 1:01 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | Manual reset & then start WTG, delay due to facing pandemic condition Covid-19.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 16:51 | 16:56 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T45 | 3 | FORCE MAJEURE | 16:56 | 17:20 | 0:24 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | Manual reset & then start WTG, delay due to facing pandemic condition Covid-19.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 17:28 | 17:36 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 11:23 | 15:20 | 3:57 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 18:31 | 18:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 18:40 | 22:41 | 4:01 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-14 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 11:25 | 11:29 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
DJ Malpani | 2021-05-14 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:18 | 15:51 | 2:33 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset & start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 17:14 | 17:18 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:14 | 15:18 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:24 | 15:28 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 16:28 | 17:38 | 1:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 19:37 | 19:41 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 20:03 | 22:16 | 2:13 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 22:30 | 22:34 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 22:38 | 22:42 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 0:06 | 0:14 | 0:08 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 1:12 | 1:16 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 1:27 | 1:31 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 1:34 | 1:38 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 1:53 | 2:35 | 0:42 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Manual reset & then start WTG.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 2:50 | 2:54 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 3:12 | 3:16 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 5:53 | 5:57 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 7:17 | 7:41 | 0:24 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Manual reset & then start WTG.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 8:30 | 8:34 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 10:18 | 10:22 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 10:41 | 10:45 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 11:00 | 11:07 | 0:07 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 11:25 | 11:27 | 0:02 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 12:11 | 12:15 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:06 | 13:10 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 17:24 | 17:27 | 0:03 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 18:16 | 18:35 | 0:19 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Manual reset & then start WTG.
DJ Malpani | 2021-05-18 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 14:38 | 14:42 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 14:38 | 14:42 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 18:28 | 18:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 18:54 | 19:28 | 0:34 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 7:20 | 7:28 | 0:08 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T45 | 3 | GA INT | 7:55 | 8:00 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 13:50 | 14:07 | 0:17 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Manual reset & then start WTG.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T45 | 3 | WTG | 15:11 | 15:16 | 0:05 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Auto reset.
DJ Malpani | 2021-04-05 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 12:29 | 13:35 | 1:06 | Breakdown Maintenance | 3001 | Brake chain - fuse opened. | Manual reset and start WTG.
DJ Malpani | 2021-04-05 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 18:24 | 18:35 | 0:11 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Manual reset, then start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:05 | 15:38 | 0:33 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Manual reset and start WTG.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 7:00 | 7:10 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 7:10 | 10:35 | 3:25 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 17:38 | 17:44 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 17:44 | 24:00 | 6:16 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 12:25 | 12:25 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 14:41 | 14:45 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Auto reset after grid.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 15:03 | 15:15 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:15 | 17:26 | 2:11 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 19:36 | 24:00 | 4:24 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Observed isolator misallignment issue,WIP.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 10:48 | 10:48 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Isolator misallignment issue has been rectified and start WTG.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 18:33 | 18:59 | 0:26 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG after grid.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 18:59 | 19:03 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 19:03 | 22:38 | 3:35 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG after grid.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 19:30 | 19:42 | 0:12 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 21:19 | 21:27 | 0:08 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Auto reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 13:15 | 13:25 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 13:25 | 14:40 | 1:15 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 16:43 | 16:53 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 16:53 | 22:49 | 5:56 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and then start WTG.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:10 | 15:14 | 0:04 | Breakdown Maintenance | 12012 | Hub Healthcheck: Blade 1 friction torque too high | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:15 | 15:29 | 0:14 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 16:53 | 24:00 | 7:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 17:15 | 17:15 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Checked related parameters found spyder coupler damaged of pump motor, then replaced it and start WTG.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 17:19 | 17:41 | 0:22 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Manual reset and start WTG.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 17:41 | 23:07 | 5:26 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Manual reset and start WTG.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 23:18 | 23:22 | 0:04 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Manual reset and start WTG.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 23:28 | 24:00 | 0:32 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | WIP, WTG unable to attend due to vehicle ROW and road bad condition due to heavy rain on site.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | WIP, WTG unable to attend due to security ROW at site.
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | WIP, Unable to attend WTG due to vehicle ROW.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 11:40 | 11:40 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Replaced Gear box oil input sensor and start the WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 15:26 | 15:37 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 16:22 | 16:40 | 0:18 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 16:41 | 16:49 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 17:00 | 17:09 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 17:48 | 24:00 | 6:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 3:08 | 3:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset delayed due to Vehicle ROW.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 6:55 | 6:59 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 6:59 | 12:15 | 5:16 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset delayed due to Vehicle ROW.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 12:57 | 13:01 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 13:09 | 13:13 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 13:39 | 14:05 | 0:26 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 14:16 | 14:20 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 17:15 | 24:00 | 6:45 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 0:00 | 22:30 | 22:30 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Manual reset.
DJ Malpani | 2021-05-02 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 7:57 | 22:33 | 14:36 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Manual reset.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T46 | 3 | FORCE MAJEURE | 0:41 | 2:44 | 2:03 | Covid 19 | 9045 | Gearbox oil input pressure below error limit. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T46 | 3 | FORCE MAJEURE | 13:58 | 17:12 | 3:14 | Covid 19 | 9045 | Gearbox oil input pressure below error limit. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 17:12 | 17:16 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T46 | 3 | FORCE MAJEURE | 17:16 | 24:00 | 6:44 | Covid 19 | 9045 | Gearbox oil input pressure below error limit. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T46 | 3 | FORCE MAJEURE | 0:00 | 5:33 | 5:33 | Covid 19 | 9045 | Gearbox oil input pressure below error limit. | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 6:24 | 6:26 | 0:02 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 6:28 | 6:36 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 11:02 | 13:08 | 2:06 | Internal Shutdown | IG01 | Internal shutdown | LC taken by Inox for restoration of isolator work at MV2T38.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T46 | 3 | FORCE MAJEURE | 15:28 | 24:00 | 8:32 | Covid 19 | 9045 | Gearbox oil input pressure below error limit. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T46 | 3 | FORCE MAJEURE | 0:00 | 2:45 | 2:45 | Covid 19 | 9045 | Gearbox oil input pressure below error limit. | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 17:58 | 18:03 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 18:03 | 23:35 | 5:32 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 16:15 | 16:22 | 0:07 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 19:01 | 19:02 | 0:01 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T46 | 3 | FORCE MAJEURE | 13:21 | 14:58 | 1:37 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | Manual reset, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T46 | 3 | FORCE MAJEURE | 22:00 | 24:00 | 2:00 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T46 | 3 | FORCE MAJEURE | 0:00 | 12:33 | 12:33 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | Checked & found yaw twist switch activated,then released & removed cable twist & then start WTG.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 15:19 | 15:35 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:35 | 17:12 | 1:37 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 7:42 | 11:30 | 3:48 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 11:30 | 12:30 | 1:00 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 4:40 | 4:50 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 5:18 | 19:50 | 14:32 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 19:50 | 20:25 | 0:35 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 20:51 | 22:10 | 1:19 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 15:44 | 15:50 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 16:51 | 16:56 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 16:56 | 17:25 | 0:29 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 16:57 | 17:01 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 18:31 | 18:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 18:40 | 22:26 | 3:46 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 17:45 | 17:49 | 0:04 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:13 | 15:17 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:31 | 15:35 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:41 | 15:58 | 0:17 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 16:10 | 16:28 | 0:18 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 16:28 | 17:38 | 1:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 19:54 | 19:58 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 18:28 | 18:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 18:41 | 18:54 | 0:13 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 18:54 | 19:28 | 0:34 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 4:43 | 4:49 | 0:06 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 5:13 | 5:17 | 0:04 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 5:56 | 6:02 | 0:06 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 6:05 | 6:09 | 0:04 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 6:26 | 6:30 | 0:04 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 6:35 | 6:39 | 0:04 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 7:33 | 7:37 | 0:04 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | GA INT | 7:55 | 8:00 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 8:03 | 8:07 | 0:04 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 10:54 | 11:06 | 0:12 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 11:26 | 11:36 | 0:10 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:21 | 15:25 | 0:04 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 15:51 | 15:55 | 0:04 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 18:35 | 22:24 | 3:49 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Manual reset & then start WTG.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 22:47 | 23:02 | 0:15 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 23:20 | 23:24 | 0:04 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T46 | 3 | WTG | 23:50 | 23:55 | 0:05 | Breakdown Maintenance | 11007 | Power deviation delayed between power measurement device and converter above limit. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 3:32 | 3:36 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 15:11 | 15:33 | 0:22 | Breakdown Maintenance | 12038 | Blade 1: Blade state plausibility. | Manual reset and start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 13:38 | 13:42 | 0:04 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 13:45 | 13:49 | 0:04 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 14:02 | 16:36 | 2:34 | Breakdown Maintenance | 12049 | Blade 1: Safety run is active. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 17:02 | 17:20 | 0:18 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Manual reset and start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 18:42 | 18:47 | 0:05 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Manual reset and start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 18:54 | 18:58 | 0:04 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 19:02 | 24:00 | 4:58 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | WIP.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 0:00 | 0:51 | 0:51 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 7:00 | 7:10 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 7:10 | 11:12 | 4:02 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 11:14 | 13:39 | 2:25 | Preventive Maintenance |  |  | USS YPM work done.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 17:48 | 17:52 | 0:04 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 18:05 | 22:28 | 4:23 | Breakdown Maintenance | 12041 | Blade 1: IPS was active in wrong area. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 17:38 | 17:44 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 17:44 | 24:00 | 6:16 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 0:00 | 12:40 | 12:40 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 13:31 | 13:35 | 0:04 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 13:42 | 13:46 | 0:04 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 14:11 | 15:44 | 1:33 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | Manual reset and start WTG.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 17:00 | 24:00 | 7:00 | Breakdown Maintenance | 0 | Grid Loss | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 0:00 | 15:03 | 15:03 | Breakdown Maintenance | 0 | Grid Loss | Manual reset & Start WTG(delayed due to vehicle ROW and bad road condition due to rain)
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 15:03 | 15:15 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 15:15 | 17:25 | 2:10 | Breakdown Maintenance | 0 | Grid Loss | Manual reset & Start WTG(delayed due to vehicle ROW and bad road condition due to rain)
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 18:59 | 19:03 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 19:03 | 23:15 | 4:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG after grid.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 10:20 | 22:58 | 12:38 | Special Activity | SA13 | Special Activity - Blade Retrofittment | One blade repair work has been completed and start WTG.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 10:15 | 17:50 | 7:35 | Special Activity | SA13 | Special Activity - Blade Retrofittment | One blade repair work has been completed and start WTG.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 18:19 | 18:22 | 0:03 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 22:10 | 22:14 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Auto reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 9:30 | 13:15 | 3:45 | Special Activity | SA13 | Special Activity - Blade Retrofittment | One blade repair work has been completed and start WTG.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 13:15 | 13:25 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 13:25 | 21:35 | 8:10 | Special Activity | SA13 | Special Activity - Blade Retrofittment | One blade repair work has been completed and start WTG.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 9:29 | 14:45 | 5:16 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Blade repair work has been completed and start WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 16:43 | 16:53 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 16:53 | 23:25 | 6:32 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and then start WTG.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 16:53 | 24:00 | 7:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 0:00 | 0:14 | 0:14 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & start WTG(Delay due to vehicle ROW and road bad condition due to heavy rain on site).
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 17:49 | 17:51 | 0:02 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 15:26 | 15:37 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 15:40 | 16:25 | 0:45 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 17:00 | 17:09 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 0:00 | 2:31 | 2:31 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset delayed due to Vehicle ROW.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 6:55 | 6:59 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 6:59 | 12:05 | 5:06 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset, delayed due to Vehicle ROW.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 17:12 | 17:16 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T49 | 3 | FORCE MAJEURE | 17:48 | 20:50 | 3:02 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 11:02 | 13:08 | 2:06 | Internal Shutdown | IG01 | Internal shutdown | LC taken by Inox for restoration of isolator work at MV2T38.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 13:08 | 15:21 | 2:13 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 17:58 | 18:03 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 18:03 | 23:50 | 5:47 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 16:15 | 16:22 | 0:07 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 18:57 | 19:03 | 0:06 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 17:51 | 17:55 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 15:19 | 15:35 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 15:35 | 16:50 | 1:15 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 7:42 | 11:30 | 3:48 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 11:30 | 12:13 | 0:43 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 4:40 | 4:50 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 4:50 | 19:50 | 15:00 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 19:50 | 20:25 | 0:35 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 20:25 | 22:00 | 1:35 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 15:44 | 15:50 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 16:51 | 16:56 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 16:56 | 17:30 | 0:34 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 17:25 | 17:55 | 0:30 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 18:31 | 18:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 18:40 | 22:20 | 3:40 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 15:31 | 15:35 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 15:41 | 15:45 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 16:28 | 17:38 | 1:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 18:34 | 18:38 | 0:04 | Breakdown Maintenance |  |  | Auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 18:28 | 18:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 18:54 | 19:28 | 0:34 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 19:58 | 20:05 | 0:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder charged manual reset & start WTG.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T49 | 3 | GA INT | 7:55 | 8:00 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T49 | 3 | WTG | 8:00 | 10:00 | 2:00 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:17 | 13:26 | 0:09 | Breakdown Maintenance | 31021 | Blade teeth lubrication is in maintenance state. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-04 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:25 | 13:44 | 0:19 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 21:17 | 21:21 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 15:06 | 15:39 | 0:33 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 7:00 | 7:10 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 7:10 | 7:20 | 0:10 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 12:56 | 13:00 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:44 | 13:55 | 0:11 | Breakdown Maintenance | 31013 | Blade bearing lubrication is in maintenance state. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 14:09 | 14:17 | 0:08 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 15:00 | 16:44 | 1:44 | Preventive Maintenance |  |  | USS YPM work done.
Giriraj Enterprises | 2021-04-08 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:56 | 23:00 | 0:04 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | Auto reset.
Giriraj Enterprises | 2021-04-08 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 23:41 | 23:45 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-08 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 23:51 | 24:00 | 0:09 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 0:12 | 0:12 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:24 | 0:28 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 9:18 | 9:22 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 9:30 | 9:34 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 9:47 | 11:15 | 1:28 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 11:28 | 17:38 | 6:10 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 17:38 | 17:44 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:44 | 24:00 | 6:16 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-10 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 18:00 | 18:00 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 21:02 | 23:59 | 2:57 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 15:03 | 15:03 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | Delayed due to vehicle ROW and bad road condition due to rain.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 15:03 | 15:15 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 15:15 | 24:00 | 8:45 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | Delayed due to vehicle ROW and bad road condition due to rain.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 13:21 | 13:21 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | Removed cable twist set YCD and took production trail and start WTG (delayed due to bad road condition due to rain)
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:57 | 18:01 | 0:04 | Breakdown Maintenance | 7171 | Converter GSA: Pole 2 hardware detected over current fault | Auto reset.
Giriraj Enterprises | 2021-04-15 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:32 | 13:41 | 0:09 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
Giriraj Enterprises | 2021-04-15 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 18:32 | 18:36 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-15 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 18:59 | 19:03 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:55 | 22:59 | 0:04 | Breakdown Maintenance | 7171 | Converter GSA: Pole 2 hardware detected over current fault | Auto reset.
Giriraj Enterprises | 2021-04-19 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 13:15 | 13:25 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-19 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:25 | 13:29 | 0:04 | Breakdown Maintenance | 7171 | Converter GSA: Pole 2 hardware detected over current fault | Auto reset.
Giriraj Enterprises | 2021-04-19 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 20:21 | 20:25 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-20 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:55 | 23:59 | 1:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 1:25 | 1:25 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 6:06 | 6:10 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 6:15 | 6:19 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 9:40 | 9:44 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 11:14 | 11:18 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 12:36 | 13:10 | 0:34 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 14:15 | 14:29 | 0:14 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 15:09 | 17:06 | 1:57 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 1:00 | 1:23 | 0:23 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 1:41 | 1:45 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 1:50 | 1:54 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 1:58 | 2:02 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 2:06 | 2:35 | 0:29 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 3:44 | 3:48 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 3:59 | 4:03 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 4:10 | 4:14 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 4:18 | 4:22 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 4:38 | 4:42 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 4:46 | 4:50 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 5:02 | 6:32 | 1:30 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 6:45 | 6:58 | 0:13 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 7:25 | 7:29 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 7:35 | 12:21 | 4:46 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Checked all parameter and hard reboot ,then start WTG.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 16:25 | 22:23 | 5:58 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-23 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 6:21 | 6:56 | 0:35 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset and then start WTG.
Giriraj Enterprises | 2021-04-23 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 7:09 | 24:00 | 16:51 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 5:01 | 5:01 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset and then start WTG.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 16:43 | 16:53 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 18:41 | 20:54 | 2:13 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset and then start WTG.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 23:01 | 23:30 | 0:29 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset and then start WTG.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:20 | 4:52 | 4:32 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | PLC reboot and reset.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 10:50 | 15:50 | 5:00 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | WIP.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 16:04 | 24:00 | 7:56 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | WIP.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | WIP, WTG unable to attend due to vehicle ROW and road bad condition due to heavy rain on site.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | WIP, WTG unable to attend due to security ROW at site.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 17:46 | 17:46 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | We checked and found cable twisted and YCD limit switch tripped, so cable twist removed and set YCD properly, then start WTG.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:58 | 23:02 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:23 | 13:27 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 14:53 | 14:54 | 0:01 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 14:58 | 15:06 | 0:08 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 15:26 | 15:37 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 16:01 | 16:09 | 0:08 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 17:00 | 17:09 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:23 | 17:27 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:33 | 17:37 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:42 | 24:00 | 6:18 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 6:47 | 6:47 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Reboot PLC and manually reset, then start WTG.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 6:55 | 6:59 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 7:27 | 7:31 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 12:22 | 12:32 | 0:10 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Manual reset.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:55 | 13:59 | 0:04 | Breakdown Maintenance | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Auto reset.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:54 | 24:00 | 1:06 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP. WTG unable to attend due to Vehicle ROW at site.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 0:31 | 0:31 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 3:31 | 14:20 | 10:49 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset delayed due to Vehicle ROW.
Giriraj Enterprises | 2021-05-01 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 14:27 | 22:34 | 8:07 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset delayed due to Vehicle ROW.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T50 | 3 | FORCE MAJEURE | 7:49 | 9:05 | 1:16 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 17:12 | 17:16 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:47 | 17:51 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 3:48 | 3:52 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T50 | 3 | FORCE MAJEURE | 7:49 | 9:05 | 1:16 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 11:02 | 13:08 | 2:06 | Internal Shutdown | IG01 | Internal shutdown | LC taken by Inox for restoration of isolator work at MV2T38.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:37 | 13:41 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 14:31 | 14:35 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:47 | 17:49 | 0:02 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 17:58 | 18:03 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T50 | 3 | FORCE MAJEURE | 18:31 | 19:33 | 1:02 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Manual reset, delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T50 | 3 | FORCE MAJEURE | 20:20 | 22:10 | 1:50 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Manual reset, delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 3:37 | 3:41 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 16:15 | 16:22 | 0:07 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 16:53 | 16:57 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 16:09 | 16:12 | 0:03 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 16:52 | 16:56 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:23 | 17:27 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 19:03 | 19:07 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 19:12 | 19:28 | 0:16 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 20:09 | 20:26 | 0:17 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:21 | 22:25 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:31 | 22:35 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:41 | 22:52 | 0:11 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T50 | 3 | FORCE MAJEURE | 19:56 | 24:00 | 4:04 | Covid 19 | 31013 | Blade bearing lubrication is in maintenance state. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T50 | 3 | FORCE MAJEURE | 0:00 | 0:11 | 0:11 | Covid 19 | 31013 | Blade bearing lubrication is in maintenance state. | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 12:23 | 12:27 | 0:04 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Auto reset.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 15:19 | 15:35 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 15:39 | 15:43 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after resume feeder.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 7:42 | 11:30 | 3:48 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 11:32 | 11:42 | 0:10 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after feeder resume.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 12:01 | 12:13 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 23:51 | 23:55 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:01 | 0:03 | 0:02 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:07 | 1:16 | 1:09 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 1:28 | 1:45 | 0:17 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 1:57 | 2:01 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 2:04 | 2:08 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 2:12 | 4:40 | 2:28 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 4:40 | 4:50 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 4:50 | 5:57 | 1:07 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 6:33 | 6:45 | 0:12 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 6:55 | 7:58 | 1:03 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 15:41 | 15:50 | 0:09 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 18:37 | 18:41 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 19:50 | 20:25 | 0:35 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 20:50 | 20:54 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:20 | 22:57 | 0:37 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 23:25 | 23:29 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T50 | 3 | FORCE MAJEURE | 23:33 | 24:00 | 0:27 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T50 | 3 | FORCE MAJEURE | 0:00 | 15:35 | 15:35 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | PLC reboot,reset manually & restored WTG, delay due to facing pandemic condition Covid-19.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 15:44 | 15:50 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 16:51 | 16:56 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:24 | 17:28 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 19:24 | 20:41 | 1:17 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 21:07 | 24:00 | 2:53 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 0:42 | 0:42 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 1:00 | 6:53 | 5:53 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 18:31 | 18:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 18:40 | 18:44 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after resume feeder.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 19:11 | 19:15 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-14 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:51 | 0:55 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 5:14 | 5:18 | 0:04 | Breakdown Maintenance | 7171 | Converter GSA: Pole 2 hardware detected over current fault | Auto reset.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 15:31 | 15:35 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 15:41 | 15:59 | 0:18 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 16:28 | 17:38 | 1:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 17:45 | 17:49 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
Giriraj Enterprises | 2021-05-17 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:25 | 13:29 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-17 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:50 | 13:54 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-17 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 15:28 | 15:32 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-17 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 20:54 | 20:58 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 13:32 | 18:59 | 5:27 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 19:38 | 19:42 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 19:46 | 20:47 | 1:01 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 22:09 | 24:00 | 1:51 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 18:28 | 18:28 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 18:28 | 18:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 18:33 | 18:54 | 0:21 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 18:54 | 19:28 | 0:34 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 19:28 | 24:00 | 4:32 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 0:00 | 7:55 | 7:55 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Checked related circuit communication cable, setting done can communication, after start WTG.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T50 | 3 | GA INT | 7:55 | 8:00 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 8:00 | 8:04 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Checked related circuit communication cable, setting done can communication, after start WTG.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T50 | 3 | WTG | 12:43 | 24:00 | 11:17 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | WIP.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 3:02 | 3:18 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Tripped Due to E/F. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 3:20 | 11:02 | 7:42 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid manual reset and start WTG.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 11:02 | 11:07 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 11:07 | 11:11 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 11:11 | 12:50 | 1:39 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid manual reset and start WTG.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 13:48 | 13:52 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 15:06 | 15:11 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 17:42 | 19:07 | 1:25 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 19:07 | 19:12 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 19:12 | 21:48 | 2:36 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-08 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 10:25 | 13:00 | 2:35 | Preventive Maintenance |  |  | USS YPM work done.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 9:50 | 9:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 9:55 | 24:00 | 14:05 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-10 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 0:00 | 4:28 | 4:28 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 4:28 | 4:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 4:34 | 24:00 | 19:26 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 0:00 | 8:18 | 8:18 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 8:18 | 8:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 8:23 | 12:30 | 4:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 9:53 | 10:01 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 10:48 | 13:58 | 3:10 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 14:00 | 14:07 | 0:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 14:19 | 14:25 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 14:48 | 18:00 | 3:12 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 15:17 | 15:44 | 0:27 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 16:35 | 16:39 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 16:43 | 16:51 | 0:08 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 19:22 | 19:26 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 19:37 | 19:41 | 0:04 | Breakdown Maintenance | 18001 | Deviation between active and demanded power is too high. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 20:35 | 24:00 | 3:25 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Delayed due to vehicle ROW and bad road condition due to rain.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 0:00 | 16:39 | 16:39 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Reboot PLC,removed cable twist set YCD and took production trail and start WTG (delayed due to bad road condition due to rain)
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 16:39 | 16:43 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 16:43 | 17:00 | 0:17 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Reboot PLC,removed cable twist set YCD and took production trail and start WTG (delayed due to bad road condition due to rain)
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 18:21 | 18:26 | 0:05 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 4:40 | 4:47 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 4:47 | 4:51 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 5:00 | 5:08 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 15:43 | 15:48 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 15:48 | 15:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 16:00 | 16:08 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 18:50 | 18:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 18:55 | 18:59 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 19:06 | 19:14 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 14:00 | 20:25 | 6:25 | Internal Shutdown | IG01 | Internal shutdown | Line clearance taken by Inox. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 20:25 | 24:00 | 3:35 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
Giriraj Enterprises | 2021-04-19 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 0:00 | 1:05 | 1:05 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 11:09 | 11:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 6:14 | 6:20 | 0:06 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 6:20 | 6:30 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 8:11 | 8:19 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-24 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 1:35 | 1:39 | 0:04 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Auto reset.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 16:53 | 23:42 | 6:49 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 15:30 | 15:38 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Auto reset.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 15:41 | 16:41 | 1:00 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 16:41 | 16:53 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid resume , WTG auto reset.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 20:15 | 20:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 20:20 | 20:28 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid resume , WTG auto reset.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 21:28 | 21:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 21:34 | 21:42 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid resume , WTG auto reset.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 22:40 | 23:02 | 0:22 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 6:07 | 6:15 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 7:53 | 8:16 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 12:14 | 12:22 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 12:30 | 12:45 | 0:15 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 14:28 | 14:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 16:04 | 16:10 | 0:06 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 9:35 | 9:43 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 10:27 | 10:35 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 10:31 | 10:39 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 10:47 | 10:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 11:25 | 11:33 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 17:26 | 17:34 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 17:49 | 17:54 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 18:27 | 18:35 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 10:05 | 10:09 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 10:13 | 10:21 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 10:25 | 11:42 | 1:17 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 11:56 | 12:04 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 12:12 | 12:20 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 12:26 | 12:34 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 12:40 | 12:48 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 13:53 | 14:01 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 14:18 | 14:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 14:50 | 17:48 | 2:58 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 17:53 | 24:00 | 6:07 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 0:00 | 1:55 | 1:55 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 2:07 | 2:47 | 0:40 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 2:59 | 3:03 | 0:04 | Breakdown Maintenance | 7001 | Converter LSA: CAN bus off fault | Auto reset.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 4:06 | 14:50 | 10:44 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-04 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 14:50 | 24:00 | 9:10 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 0:00 | 2:11 | 2:11 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Manual reset, delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 2:13 | 4:42 | 2:29 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Manual reset, delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-05 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 4:45 | 24:00 | 19:15 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 0:00 | 15:38 | 15:38 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 15:38 | 16:19 | 0:41 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 16:19 | 19:20 | 3:01 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 19:20 | 22:50 | 3:30 | Feeder tripped E/F | IG02 | Earth Fault | Tripped due to E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 22:50 | 24:00 | 1:10 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 0:00 | 12:45 | 12:45 | Covid 19 | 7001 | Converter LSA: CAN bus off fault | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 12:45 | 14:23 | 1:38 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 23:31 | 23:55 | 0:24 | Breakdown Maintenance | 7140 | Converter GSA: Power Supply Fault 24V | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 4:58 | 17:50 | 12:52 | Covid 19 | 7534 | Converter system detected line voltage error. | Manual reset, delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 18:35 | 24:00 | 5:25 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, trial not taken due to VCB Y pole stuck.WIP.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 0:00 | 14:18 | 14:18 | Feeder tripped O/C | IG03 | Over Current | Tripped by O/C, circuit breaker pole change, then checked & charged feeder ok.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 20:13 | 20:17 | 0:04 | Breakdown Maintenance | 27006 | Converter cooling water pressure low alarm. | Auto reset
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 23:26 | 24:00 | 0:34 | Covid 19 | 27006 | Converter cooling water pressure low alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 0:00 | 0:57 | 0:57 | Covid 19 | 27006 | Converter cooling water pressure low alarm. | Checked related all parameters and also checked pressure of converter coolant found ok, then reset and start WTG.
Giriraj Enterprises | 2021-05-10 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 2:19 | 24:00 | 21:41 | Covid 19 | 27006 | Converter cooling water pressure low alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 0:00 | 13:13 | 13:13 | Covid 19 | 27006 | Converter cooling water pressure low alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 13:13 | 13:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 13:18 | 19:25 | 6:07 | Covid 19 | 27006 | Converter cooling water pressure low alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 19:25 | 23:33 | 4:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 23:33 | 24:00 | 0:27 | Covid 19 | 27006 | Converter cooling water pressure low alarm. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T57 | 8 | FORCE MAJEURE | 0:00 | 5:35 | 5:35 | Covid 19 | 27006 | Converter cooling water pressure low alarm. | Manual reset & then start WTG, delay due to facing pandemic condition Covid-19.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 5:42 | 5:46 | 0:04 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 5:50 | 5:54 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 5:58 | 6:24 | 0:26 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 18:19 | 18:27 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 18:32 | 18:37 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 18:37 | 18:45 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after feeder resume
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 5:44 | 5:52 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 6:00 | 6:05 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 9:37 | 12:18 | 2:41 | Breakdown Maintenance | 27006 | Converter cooling water pressure low alarm. | Topped up coolant and checked for any abnormalities and start WTG.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 12:18 | 14:21 | 2:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 14:21 | 15:19 | 0:58 | Breakdown Maintenance | 27006 | Converter cooling water pressure low alarm. | Topped up coolant and checked for any abnormalities and start WTG.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 15:19 | 16:50 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 16:50 | 19:15 | 2:25 | Breakdown Maintenance | 27006 | Converter cooling water pressure low alarm. | Topped up coolant and checked for any abnormalities and start WTG.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 6:14 | 6:22 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 8:29 | 8:34 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 10:55 | 11:03 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 11:24 | 11:28 | 0:04 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 11:41 | 11:49 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 12:12 | 12:20 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 12:37 | 12:45 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 13:12 | 13:17 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 13:56 | 14:04 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 14:44 | 14:52 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 15:29 | 15:31 | 0:02 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 15:46 | 15:54 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 16:16 | 16:21 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 16:21 | 17:06 | 0:45 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 17:06 | 17:10 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 17:15 | 17:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-17 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | WIP
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 0:00 | 14:45 | 14:45 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | WIP
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 14:45 | 18:25 | 3:40 | Internal Shutdown | IG01 | Internal shutdown | Shutdown taken for tree cutting work.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 18:25 | 24:00 | 5:35 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | WIP
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 0:00 | 11:51 | 11:51 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | PLC reboot and reset then start WTG.
Giriraj Enterprises | 2021-05-19 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 12:51 | 24:00 | 11:09 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | WIP.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 0:00 | 8:13 | 8:13 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | Replaced online filter after start WTG.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T57 | 8 | GA INT | 8:13 | 8:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 8:18 | 14:30 | 6:12 | Breakdown Maintenance | 9037 | Gearbox oil filter clogging sensors detect a "not plausible" state. | Replaced online filter after start WTG.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T57 | 8 | WTG | 17:10 | 24:00 | 6:50 | Breakdown Maintenance | 27003 | High error of converter cooling water output temperature. | WIP.
DJ Malpani | 2021-04-02 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 14:57 | 15:00 | 0:03 | Breakdown Maintenance | 7140 | Converter GSA: Power Supply Fault 24V | Manual reset and start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 15:08 | 15:12 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 7:00 | 7:10 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-07 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 7:10 | 7:18 | 0:08 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 17:38 | 17:44 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 17:46 | 17:50 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 8:22 | 8:30 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 17:00 | 24:00 | 7:00 | Breakdown Maintenance | 0 | Grid Loss | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 0:00 | 15:03 | 15:03 | Breakdown Maintenance | 0 | Grid Loss | Manual reset & start WTG (delayed due to vehicle row and bad road condition due to rain).
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 15:03 | 15:15 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 15:15 | 18:42 | 3:27 | Breakdown Maintenance | 0 | Grid Loss | Manual reset & start WTG (delayed due to vehicle row and bad road condition due to rain).
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 18:34 | 18:38 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 18:59 | 19:03 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 10:49 | 10:53 | 0:04 | Breakdown Maintenance | 7140 | Converter GSA: Power Supply Fault 24V | Auto reset.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 13:15 | 13:25 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 13:27 | 13:31 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 0:54 | 12:29 | 11:35 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | Yaw twist setting done and cable twist remove, then start the WTG.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 16:43 | 16:53 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 10:50 | 15:50 | 5:00 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | WIP.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 16:04 | 24:00 | 7:56 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | WIP.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | WIP, WTG unable to attend due to vehicle ROW and road bad condition due to heavy rain on site.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | WIP, WTG unable to attend due to security ROW at site.
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 0:00 | 17:00 | 17:00 | Breakdown Maintenance | 21010 | Safety chain - Yaw twist protection triggered. | We checked and found cable twisted and YCD limit switch tripped, so cable twist removed and set YCD properly, then start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 9:40 | 15:10 | 5:30 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Blade no 1280 SS side retrofitting done.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 15:26 | 15:37 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 15:33 | 15:37 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 17:00 | 17:09 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 17:05 | 17:09 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 6:55 | 6:59 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 7:00 | 7:04 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 9:40 | 24:00 | 14:20 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Blade no 1280 SS side retrofitting done, but we can't reset WTG due to Vehicle ROW.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 0:00 | 13:27 | 13:27 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Release emergency , manual start WTG.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 14:10 | 14:14 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 17:12 | 17:16 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 17:19 | 17:23 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 11:02 | 13:08 | 2:06 | Internal Shutdown | IG01 | Internal shutdown | LC taken by Inox for restoration of isolator work at MV2T38.
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 13:13 | 13:25 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 15:15 | 15:19 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 17:58 | 18:03 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 18:04 | 18:08 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 9:30 | 16:15 | 6:45 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Blade repairing work done.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 16:15 | 16:22 | 0:07 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 16:22 | 23:00 | 6:38 | Special Activity | SA13 | Special Activity - Blade Retrofittment | Blade repairing work done.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 13:23 | 13:27 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 15:12 | 15:19 | 0:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after resume feeder.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 15:19 | 15:35 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 7:42 | 11:30 | 3:48 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 11:33 | 11:44 | 0:11 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after feeder resume.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 4:40 | 4:50 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to 100MV transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 4:50 | 4:54 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 19:40 | 19:44 | 0:04 | Breakdown Maintenance | 26016 | Tower vibration (acceleration peak-to-peak value) in non-drivetrain direction delayed is above limit | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 19:50 | 20:25 | 0:35 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 20:25 | 20:27 | 0:02 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T6 | 3 | FORCE MAJEURE | 20:45 | 24:00 | 3:15 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T6 | 3 | FORCE MAJEURE | 0:00 | 15:10 | 15:10 | Covid 19 | 21010 | Safety chain - Yaw twist protection triggered. | Manual reset & then start WTG, delay due to facing pandemic condition Covid-19.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 15:44 | 15:50 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 16:51 | 16:56 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 16:57 | 17:01 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 18:31 | 18:40 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 18:44 | 18:48 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 13:20 | 13:47 | 0:27 | Breakdown Maintenance |  |  | Manual reset & then start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 14:35 | 14:43 | 0:08 | Breakdown Maintenance |  |  | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 15:48 | 15:56 | 0:08 | Breakdown Maintenance |  |  | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 16:00 | 16:08 | 0:08 | Breakdown Maintenance |  |  | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 10:39 | 10:43 | 0:04 | Breakdown Maintenance | 7140 | Converter GSA: Power Supply Fault 24V | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 14:35 | 14:39 | 0:04 | Breakdown Maintenance |  |  | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 14:43 | 15:35 | 0:52 | Breakdown Maintenance |  |  | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 16:28 | 17:38 | 1:10 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 17:38 | 18:38 | 1:00 | Breakdown Maintenance | 0 | Grid Loss | Checked and found VCB tripped, so checked related paramters, then charged VCB, then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 19:25 | 23:40 | 4:15 | Breakdown Maintenance | 0 | Grid Loss | Checked and found VCB tripped, so checked related paramters, then charged VCB, then start WTG.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 11:49 | 11:53 | 0:04 | Breakdown Maintenance |  |  | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 11:59 | 12:32 | 0:33 | Breakdown Maintenance |  |  | Manual reset & then start WTG.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 13:48 | 13:52 | 0:04 | Breakdown Maintenance |  |  | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 13:56 | 14:04 | 0:08 | Breakdown Maintenance |  |  | Auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 18:28 | 18:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 18:35 | 18:39 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | After feeder charged WTG auto reset.
DJ Malpani | 2021-05-19 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 18:54 | 19:28 | 0:34 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T6 | 3 | GA INT | 7:55 | 8:00 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T6 | 3 | WTG | 8:03 | 8:07 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 3:02 | 3:18 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Tripped Due to E/F. Checked & charged feeder ok.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 3:20 | 3:24 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid resume.
DJ Malpani | 2021-04-02 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 11:02 | 11:07 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-02 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 11:07 | 11:11 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 15:06 | 15:11 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 19:03 | 19:07 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 19:07 | 19:12 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 9:50 | 9:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 4:28 | 4:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 4:34 | 4:38 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 16:31 | 16:35 | 0:04 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 5:07 | 5:11 | 0:04 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Auto reset.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 8:18 | 8:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 17:32 | 24:00 | 6:28 | Breakdown Maintenance | 0 | Grid Loss | WIP.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 0:00 | 14:19 | 14:19 | Breakdown Maintenance | 0 | Grid Loss | WIP.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 14:19 | 14:25 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 14:25 | 24:00 | 9:35 | Breakdown Maintenance | 0 | Grid Loss | WIP.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 0:00 | 10:55 | 10:55 | Breakdown Maintenance | 0 | Grid Loss | Manual reset and start WTG (delayed due to vehicle ROW and bad road condition due to rain)
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 16:39 | 16:43 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 16:48 | 16:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 4:40 | 4:47 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 4:47 | 4:51 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 15:43 | 15:48 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 15:48 | 15:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 18:50 | 18:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 18:55 | 18:59 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 14:00 | 20:25 | 6:25 | Internal Shutdown | IG01 | Internal shutdown | Line clearance taken by Inox. Checked & charged feeder ok.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 20:25 | 24:00 | 3:35 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 0:00 | 0:40 | 0:40 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 7:21 | 7:29 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-21 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 11:09 | 11:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-21 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 11:29 | 11:41 | 0:12 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Manual reset & then start WTG.
DJ Malpani | 2021-04-22 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 6:20 | 6:30 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-22 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 6:30 | 6:33 | 0:03 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-04-22 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 8:28 | 8:32 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 16:12 | 16:24 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 15:41 | 16:41 | 1:00 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 20:15 | 20:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 21:07 | 24:00 | 2:53 | Breakdown Maintenance | 0 | Grid Loss | WIP.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 21:28 | 21:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 0:00 | 7:53 | 7:53 | Breakdown Maintenance | 0 | Grid Loss | WIP.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 7:53 | 8:16 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 8:16 | 14:28 | 6:12 | Breakdown Maintenance | 0 | Grid Loss | WIP.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 14:28 | 14:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 14:33 | 24:00 | 9:27 | Breakdown Maintenance | 0 | Grid Loss | WIP.
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 0:00 | 16:54 | 16:54 | Breakdown Maintenance | 0 | Grid Loss | Found yard VCB tripped condition charged yard VCB then start WTG(Delay due to vehicle ROW)
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 16:21 | 16:33 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 9:57 | 10:01 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 10:47 | 10:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 10:52 | 10:56 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 17:49 | 17:54 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 17:54 | 17:58 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 8:43 | 8:47 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 14:18 | 14:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 14:23 | 14:27 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 17:53 | 17:57 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 15:38 | 16:19 | 0:41 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 16:22 | 16:34 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 19:20 | 22:50 | 3:30 | Feeder tripped E/F | IG02 | Earth Fault | Tripped due to E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 22:54 | 23:06 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 12:45 | 14:23 | 1:38 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 14:26 | 14:38 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 12:44 | 12:56 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 18:35 | 24:00 | 5:25 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, trial not taken due to VCB Y pole stuck.WIP.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 0:00 | 14:18 | 14:18 | Feeder tripped O/C | IG03 | Over Current | Tripped by O/C, circuit breaker pole change, then checked & charged feeder ok.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 14:21 | 14:33 | 0:12 | Breakdown Maintenance | 31001 | Generator lubrication and yaw teeth lubrication overload switch failure. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 17:19 | 17:23 | 0:04 | Breakdown Maintenance | 1014 | Anemometer 2 communication error. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 17:25 | 17:29 | 0:04 | Breakdown Maintenance | 1014 | Anemometer 2 communication error. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 17:31 | 22:03 | 4:32 | Breakdown Maintenance | 1014 | Anemometer 2 communication error. | Manual reset & then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 13:13 | 13:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 13:18 | 13:22 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 19:25 | 23:33 | 4:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 18:32 | 18:37 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 18:37 | 18:41 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 6:00 | 6:05 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 6:06 | 6:10 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 12:18 | 14:21 | 2:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 15:19 | 16:50 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 16:38 | 16:50 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 8:29 | 8:34 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 8:34 | 8:38 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 12:20 | 13:12 | 0:52 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 13:12 | 13:17 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 13:17 | 16:16 | 2:59 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 16:16 | 16:21 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 16:21 | 16:25 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 17:06 | 17:10 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T62 | 8 | WTG | 17:10 | 17:18 | 0:08 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 17:15 | 17:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-18 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 14:45 | 18:25 | 3:40 | Internal Shutdown | IG01 | Internal shutdown | Shutdown taken for tree cutting work.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T62 | 8 | GA INT | 8:13 | 8:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 3:02 | 3:18 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Tripped Due to E/F. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-01 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 3:54 | 4:02 | 0:08 | Breakdown Maintenance | 31001 | Generator lubrication and yaw teeth lubrication overload switch failure. | Auto reset after grid resume.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 11:02 | 11:07 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 11:07 | 11:11 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-02 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 11:40 | 11:48 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 4:46 | 4:54 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-04-05 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 6:04 | 6:20 | 0:16 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Manual reset, then start WTG.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 15:06 | 15:11 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 15:36 | 15:40 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 19:07 | 19:12 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-06 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 19:37 | 19:45 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
Giriraj Enterprises | 2021-04-07 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 14:26 | 14:34 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 9:50 | 9:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-09 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 10:24 | 10:32 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 4:28 | 4:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-11 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 5:07 | 5:16 | 0:09 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-12 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 8:18 | 8:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 14:19 | 14:25 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-13 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 14:49 | 15:05 | 0:16 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 16:39 | 16:43 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 16:48 | 16:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-14 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 17:22 | 17:30 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 4:40 | 4:47 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 5:21 | 5:29 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 15:43 | 15:48 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 16:22 | 16:30 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 18:50 | 18:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-17 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 19:29 | 19:37 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 14:00 | 20:25 | 6:25 | Internal Shutdown | IG01 | Internal shutdown | Line clearance taken by Inox. Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-18 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 20:25 | 24:00 | 3:35 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
Giriraj Enterprises | 2021-04-19 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 0:00 | 0:20 | 0:20 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 11:09 | 11:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-21 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 11:59 | 12:11 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 6:20 | 6:30 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 7:02 | 7:10 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-22 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 9:01 | 9:09 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
Giriraj Enterprises | 2021-04-25 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 21:44 | 24:00 | 2:16 | Breakdown Maintenance | 0 | Grid Loss | WIP.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 0:00 | 15:41 | 15:41 | Breakdown Maintenance | 0 | Grid Loss | WIP.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 15:41 | 16:41 | 1:00 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 16:41 | 20:15 | 3:34 | Breakdown Maintenance | 0 | Grid Loss | WIP.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 20:15 | 20:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 20:20 | 21:28 | 1:08 | Breakdown Maintenance | 0 | Grid Loss | WIP.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 21:28 | 21:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
Giriraj Enterprises | 2021-04-26 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 21:34 | 24:00 | 2:26 | Breakdown Maintenance | 0 | Grid Loss | WIP.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 0:00 | 7:53 | 7:53 | Breakdown Maintenance | 0 | Grid Loss | WIP.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 7:53 | 8:16 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 8:16 | 14:28 | 6:12 | Breakdown Maintenance | 0 | Grid Loss | WIP.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 14:28 | 14:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-27 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 14:33 | 24:00 | 9:27 | Breakdown Maintenance | 0 | Grid Loss | WIP.
Giriraj Enterprises | 2021-04-28 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 0:00 | 16:07 | 16:07 | Breakdown Maintenance | 0 | Grid Loss | Found yard VCB tripped condition charged yard VCB then start WTG(Delay due to vehicle ROW)
Giriraj Enterprises | 2021-04-28 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 16:51 | 17:03 | 0:12 | Breakdown Maintenance | 31001 | Generator lubrication and yaw teeth lubrication overload switch failure. | Auto reset.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-29 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 16:51 | 17:03 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 10:31 | 10:39 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 10:47 | 10:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 11:25 | 11:33 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 17:49 | 17:54 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-04-30 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 18:27 | 18:35 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 14:18 | 14:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 14:57 | 15:05 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-03 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 18:26 | 18:34 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 15:38 | 16:19 | 0:41 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 16:52 | 17:04 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 19:20 | 22:50 | 3:30 | Feeder tripped E/F | IG02 | Earth Fault | Tripped due to E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-06 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 23:24 | 23:36 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 12:45 | 14:23 | 1:38 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 14:57 | 15:09 | 0:12 | Breakdown Maintenance | 7137 | Converter GSA: Low line fault | Auto reset.
Giriraj Enterprises | 2021-05-07 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 17:44 | 17:48 | 0:04 | Breakdown Maintenance | 7137 | Converter GSA: Low line fault | Auto reset.
Giriraj Enterprises | 2021-05-08 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 18:35 | 24:00 | 5:25 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, trial not taken due to VCB Y pole stuck.WIP.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 0:00 | 14:18 | 14:18 | Feeder tripped O/C | IG03 | Over Current | Tripped by O/C, circuit breaker pole change, then checked & charged feeder ok.
Giriraj Enterprises | 2021-05-09 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 14:51 | 15:03 | 0:12 | Breakdown Maintenance | 31001 | Generator lubrication and yaw teeth lubrication overload switch failure. | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 13:13 | 13:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 13:51 | 13:58 | 0:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-11 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 19:25 | 23:33 | 4:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 0:05 | 0:17 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T63 | 8 | FORCE MAJEURE | 5:37 | 17:40 | 12:03 | Covid 19 | 21004 | Safety chain - Fuse opened. | PLC reboot,reset manually & restored WTG, delay due to facing pandemic condition Covid-19.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 18:32 | 18:37 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-12 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 19:10 | 19:18 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 6:00 | 6:05 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 6:40 | 6:48 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 12:18 | 14:21 | 2:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 15:19 | 16:50 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-13 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 17:08 | 17:20 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 8:29 | 8:34 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 9:05 | 9:16 | 0:11 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 13:12 | 13:17 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 13:51 | 13:59 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 15:32 | 15:40 | 0:08 | Breakdown Maintenance | 30007 | Each YCD shows internal errors. | Auto reset.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 16:16 | 16:21 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 16:55 | 17:03 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 17:06 | 17:10 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-15 | Maharashtra | Vaspeth | MV2T63 | 8 | WTG | 17:44 | 17:52 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 17:15 | 17:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-16 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
Giriraj Enterprises | 2021-05-18 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 14:45 | 18:25 | 3:40 | Internal Shutdown | IG01 | Internal shutdown | Shutdown taken for tree cutting work.
Giriraj Enterprises | 2021-05-20 | Maharashtra | Vaspeth | MV2T63 | 8 | GA INT | 8:13 | 8:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 3:02 | 3:18 | 0:16 | Feeder tripped E/F | IG02 | Earth Fault | Tripped Due to E/F. Checked & charged feeder ok.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 3:20 | 10:15 | 6:55 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid manual reset and start WTG.
DJ Malpani | 2021-04-02 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 11:02 | 11:07 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-02 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 11:11 | 12:15 | 1:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After grid manual reset and start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 13:44 | 13:48 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Auto reset.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 15:06 | 15:11 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 17:37 | 19:07 | 1:30 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 19:07 | 19:12 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-06 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 19:12 | 20:57 | 1:45 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 9:50 | 9:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 9:55 | 24:00 | 14:05 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 0:00 | 4:28 | 4:28 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 4:28 | 4:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 4:34 | 24:00 | 19:26 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 0:00 | 8:18 | 8:18 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 8:18 | 8:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 8:23 | 11:30 | 3:07 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 14:19 | 14:25 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 14:54 | 17:25 | 2:31 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG after grid.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 14:04 | 14:12 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 16:39 | 16:43 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 16:48 | 16:52 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 4:40 | 4:47 | 0:07 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 5:12 | 5:23 | 0:11 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 15:43 | 15:48 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 16:08 | 16:20 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 18:50 | 18:55 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 19:11 | 19:24 | 0:13 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 14:00 | 20:25 | 6:25 | Internal Shutdown | IG01 | Internal shutdown | Line clearance taken by Inox. Checked & charged feeder ok.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 20:25 | 23:04 | 2:39 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 15:15 | 16:45 | 1:30 | Preventive Maintenance |  |  | USS YPM work done.
DJ Malpani | 2021-04-21 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 11:09 | 11:29 | 0:20 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-21 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 11:30 | 15:49 | 4:19 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset at location.
DJ Malpani | 2021-04-22 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 5:07 | 9:41 | 4:34 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset then start WTG.
DJ Malpani | 2021-04-22 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 6:20 | 6:30 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 16:53 | 23:51 | 6:58 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 13:44 | 15:41 | 1:57 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 15:41 | 16:41 | 1:00 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 16:41 | 20:15 | 3:34 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 20:15 | 20:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 20:20 | 21:28 | 1:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 21:28 | 21:34 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped due to heavy rain, checked & charged feeder ok.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 21:34 | 23:59 | 2:25 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 0:00 | 6:40 | 6:40 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 7:53 | 8:16 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 11:06 | 14:28 | 3:22 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 14:28 | 14:33 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 14:33 | 24:00 | 9:27 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP
DJ Malpani | 2021-04-28 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 0:00 | 14:55 | 14:55 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset and start WTG.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 16:30 | 24:00 | 7:30 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 9:30 | 9:38 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 10:20 | 10:28 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 10:47 | 10:52 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 17:16 | 17:24 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 17:49 | 17:54 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T9 | 8 | FORCE MAJEURE | 13:38 | 14:18 | 0:40 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 14:18 | 14:23 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T9 | 8 | FORCE MAJEURE | 14:23 | 17:48 | 3:25 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MV2T9 | 8 | FORCE MAJEURE | 17:53 | 18:58 | 1:05 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset,delay for attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 15:38 | 16:19 | 0:41 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 18:37 | 18:49 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 19:20 | 22:50 | 3:30 | Feeder tripped E/F | IG02 | Earth Fault | Tripped due to E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 12:45 | 14:23 | 1:38 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 14:57 | 15:09 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 12:44 | 12:56 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 18:35 | 24:00 | 5:25 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped on O/C, trial not taken due to VCB Y pole stuck.WIP.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 0:00 | 14:18 | 14:18 | Feeder tripped O/C | IG03 | Over Current | Tripped by O/C, circuit breaker pole change, then checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 12:36 | 12:40 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 13:13 | 13:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 14:21 | 19:10 | 4:49 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 19:25 | 23:33 | 4:08 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MV2T9 | 8 | FORCE MAJEURE | 23:33 | 24:00 | 0:27 | Covid 19 | 21004 | Safety chain - Fuse opened. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T9 | 8 | FORCE MAJEURE | 0:00 | 4:10 | 4:10 | Covid 19 | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG, delay due to facing pandemic condition Covid-19.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 18:32 | 18:37 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MV2T9 | 8 | FORCE MAJEURE | 19:02 | 22:44 | 3:42 | Covid 19 | 21004 | Safety chain - Fuse opened. | PLC reboot,reset manually & restored WTG, delay due to facing pandemic condition Covid-19.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 6:00 | 6:05 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 12:18 | 14:21 | 2:03 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 15:19 | 16:50 | 1:31 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 16:50 | 18:09 | 1:19 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 5:40 | 8:13 | 2:33 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 8:29 | 8:34 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 13:12 | 13:17 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 16:16 | 16:21 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 17:06 | 17:10 | 0:04 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 17:15 | 17:20 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 17:20 | 17:35 | 0:15 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 17:48 | 17:53 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 17:53 | 19:10 | 1:17 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 11:22 | 11:26 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-18 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 14:45 | 18:25 | 3:40 | Internal Shutdown | IG01 | Internal shutdown | Shutdown taken for tree cutting work.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T9 | 8 | GA INT | 8:13 | 8:18 | 0:05 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-20 | Maharashtra | Vaspeth | MV2T9 | 8 | WTG | 8:18 | 10:26 | 2:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 3:02 | 3:06 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 11:51 | 18:35 | 6:44 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-01 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 23:14 | 23:59 | 0:45 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-02 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 0:00 | 0:41 | 0:41 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Auto Reset.
DJ Malpani | 2021-04-02 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 7:48 | 22:55 | 15:07 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Pitch converter capacitor discharged and rebooted pitch converter and start WTG.
DJ Malpani | 2021-04-03 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 3:00 | 6:50 | 3:50 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Pitch converter capacitor discharged and rebooted pitch converter and start WTG.
DJ Malpani | 2021-04-04 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 8:05 | 14:20 | 6:15 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Blade 1 hartening connector cable replaced by old one,then start WTG.
DJ Malpani | 2021-04-09 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 14:13 | 14:17 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-04-10 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 0:00 | 23:59 | 23:59 | Breakdown Maintenance |  |  | Unknown error due to connectivity not available ,Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-11 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | Unknown error due to connectivity not available ,Unable to attend WTG, due to ROW created by vehicle vendor.
DJ Malpani | 2021-04-12 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 0:00 | 17:00 | 17:00 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Reboot and reset, then start WTG.
DJ Malpani | 2021-04-13 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 15:34 | 15:38 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset after grid.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 1:55 | 4:00 | 2:05 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 13:15 | 13:38 | 0:23 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset & start WTG.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 16:38 | 16:42 | 0:04 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Auto reset.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 19:25 | 21:50 | 2:25 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-14 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 22:18 | 24:00 | 1:42 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | WIP.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 0:00 | 1:40 | 1:40 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 3:03 | 5:30 | 2:27 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 6:00 | 15:45 | 9:45 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Manual reset and start WTG.
DJ Malpani | 2021-04-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 16:31 | 24:00 | 7:29 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Due to cable issue, awaiting for cable for normal operation.
DJ Malpani | 2021-04-16 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 0:00 | 17:30 | 17:30 | Breakdown Maintenance | 21014 | Safety chain - Hub drive error or CAN communication problem with hub drives. | Replaced hub harting and resolver cable of motor and took production trail and start WTG.
DJ Malpani | 2021-04-17 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 16:43 | 16:46 | 0:03 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 9:40 | 9:44 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-04-18 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 21:50 | 24:00 | 2:10 | Breakdown Maintenance | 0 | Grid Loss | WIP.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 0:00 | 2:00 | 2:00 | Breakdown Maintenance | 0 | Grid Loss | Manual reset at location.
DJ Malpani | 2021-04-19 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 16:32 | 16:36 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 14:01 | 14:05 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 14:46 | 14:50 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-04-20 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 17:13 | 17:17 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-04-21 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 1:36 | 1:39 | 0:03 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-22 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 13:50 | 13:54 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-22 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 17:20 | 17:24 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-23 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 8:12 | 8:16 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 8:06 | 8:15 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 8:15 | 8:19 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-24 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 12:16 | 21:52 | 9:36 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Manual reset and then start WTG.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 15:26 | 15:50 | 0:24 | Breakdown Maintenance | 0 | Grid Loss | WIP
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 15:50 | 16:04 | 0:14 | Feeder tripped E/F | IG02 | Earth Fault | 33 KV line tripped due to heavy rain , checked & charged feeder ok.
DJ Malpani | 2021-04-25 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 16:04 | 23:59 | 7:55 | Breakdown Maintenance | 0 | Grid Loss | WIP
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 0:00 | 7:17 | 7:17 | Breakdown Maintenance | 0 | Grid Loss | Found yard VCB tripped condition charged yard VCB, then start WTG.
DJ Malpani | 2021-04-26 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 17:23 | 23:59 | 6:36 | Breakdown Maintenance | 0 | Grid Loss | WIP.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 0:00 | 5:50 | 5:50 | Breakdown Maintenance | 0 | Grid Loss | Found yard VCB tripped condition, charged yard VCB, then start WTG.
DJ Malpani | 2021-04-27 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 8:19 | 8:29 | 0:10 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | WIP, WTG unable to attend due to security ROW at site.
DJ Malpani | 2021-04-29 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 15:44 | 15:48 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 9:52 | 9:56 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 13:13 | 13:17 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 18:05 | 18:11 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-04-30 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 18:11 | 18:15 | 0:04 | Breakdown Maintenance | 7534 | Converter system detected line voltage error. | Auto reset after grid.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 8:44 | 8:49 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-01 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 8:49 | 8:52 | 0:03 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 17:44 | 17:48 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 17:53 | 17:58 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 17:58 | 18:01 | 0:03 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 18:13 | 18:17 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
DJ Malpani | 2021-05-03 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 18:41 | 18:45 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset
DJ Malpani | 2021-05-04 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 8:03 | 10:50 | 2:47 | Breakdown Maintenance | 30013 | Hydraulic brake pressure sensors are defective. | Auto reset.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MVT80 | 5 | FORCE MAJEURE | 14:14 | 14:52 | 0:38 | Covid 19 | 30013 | Hydraulic brake pressure sensors are defective. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 14:52 | 14:58 | 0:06 | Feeder tripped E/F | IG02 | Earth Fault | Checked & charged feeder ok.
DJ Malpani | 2021-05-05 | Maharashtra | Vaspeth | MVT80 | 5 | FORCE MAJEURE | 14:58 | 24:00 | 9:02 | Covid 19 | 30013 | Hydraulic brake pressure sensors are defective. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MVT80 | 5 | FORCE MAJEURE | 0:00 | 6:20 | 6:20 | Covid 19 | 30013 | Hydraulic brake pressure sensors are defective. | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 15:40 | 16:20 | 0:40 | Feeder tripped E/F | IG02 | Earth Fault | Tripped due to E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 16:23 | 16:35 | 0:12 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 19:20 | 22:50 | 3:30 | Feeder tripped E/F | IG02 | Earth Fault | 100 MVA transformer LV tripped, Checked & charged feeder ok.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 22:55 | 23:10 | 0:15 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | After feeder resume WTG auto reset.
DJ Malpani | 2021-05-06 | Maharashtra | Vaspeth | MVT80 | 5 | FORCE MAJEURE | 23:10 | 24:00 | 0:50 | Covid 19 | 7529 | Converter system crowbar test failed. | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-07 | Maharashtra | Vaspeth | MVT80 | 5 | FORCE MAJEURE | 0:00 | 22:15 | 22:15 | Covid 19 | 7529 | Converter system crowbar test failed. | PLC reboot,reset manually & restored WTG, delay for attend attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-08 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 19:13 | 19:21 | 0:08 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 15:16 | 15:27 | 0:11 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F, Checked & charged feeder ok.
DJ Malpani | 2021-05-09 | Maharashtra | Vaspeth | MVT80 | 5 | FORCE MAJEURE | 15:27 | 24:00 | 8:33 | Covid 19 | 0 | Grid Loss | Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MVT80 | 5 | FORCE MAJEURE | 0:00 | 13:21 | 13:21 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Checked and found VCB tripped, so checked related parameters not found any abnormalities, so charged VCB, then start WTG.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 13:21 | 13:26 | 0:05 | Feeder tripped E/F | IG02 | Earth Fault | Feeder tripped by E/F.
DJ Malpani | 2021-05-10 | Maharashtra | Vaspeth | MVT80 | 5 | FORCE MAJEURE | 13:26 | 18:25 | 4:59 | Covid 19 | 22013 | Speed measurement deviation between rotor encoder and analogue feedback. | Checked and found VCB tripped, so checked related parameters not found any abnormalities, so charged VCB, then start WTG.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MVT80 | 5 | GA INT | 12:07 | 12:21 | 0:14 | Feeder tripped O/C | IG03 | Over Current | Feeder tripped by O/C, Checked & charged feeder ok.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 12:23 | 12:31 | 0:08 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 19:24 | 19:28 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Auto reset.
DJ Malpani | 2021-05-11 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 19:34 | 19:38 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 13:36 | 13:40 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-12 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 15:50 | 15:54 | 0:04 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Auto reset.
DJ Malpani | 2021-05-13 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 5:57 | 6:36 | 0:39 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Manual reset & then start WTG.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 11:35 | 11:39 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 12:20 | 12:22 | 0:02 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 12:41 | 12:45 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 12:50 | 12:54 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 14:06 | 14:10 | 0:04 | Breakdown Maintenance | 11001 | Active power above limit. | Auto reset.
DJ Malpani | 2021-05-15 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 14:35 | 17:03 | 2:28 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 7:47 | 12:42 | 4:55 | Breakdown Maintenance | 11001 | Active power above limit. | Manual reset & then start WTG.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 15:46 | 15:50 | 0:04 | Breakdown Maintenance | 11001 | Active power above limit. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 17:09 | 17:13 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 17:17 | 17:21 | 0:04 | Breakdown Maintenance | 11001 | Active power above limit. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 21:03 | 21:07 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-16 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 21:12 | 21:16 | 0:04 | Breakdown Maintenance | 21004 | Safety chain - Fuse opened. | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 1:02 | 9:15 | 8:13 | Breakdown Maintenance | 11001 | Active power above limit. | Manual reset & then start WTG.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 9:47 | 9:51 | 0:04 | Breakdown Maintenance | 26014 | Tower-vibration (acceleration peak-to-peak value) for non-drivetrain direction above alarm limit | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 10:16 | 10:20 | 0:04 | Breakdown Maintenance | 7011 | Converter LSA: Hardware detected DC bus over voltage fault | Auto reset.
DJ Malpani | 2021-05-17 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 10:26 | 14:42 | 4:16 | Breakdown Maintenance | 11001 | Active power above limit. | Manual reset & then start WTG.
DJ Malpani | 2021-05-18 | Maharashtra | Vaspeth | MVT80 | 5 | WTG | 4:54 | 4:58 | 0:04 | Breakdown Maintenance | 30006 | Nacelle rotation overspeed. | Auto reset.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT02 | 4 | WTG | 15:13 | 16:36 | 1:23 | Breakdown Maintenance |  |  | Attend and found all releted check ckt and found connection loose so rectionfication work done than start wtg.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT02 | 4 | WTG | 19:25 | 19:33 | 0:08 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT02 | 4 | WTG | 19:40 | 19:48 | 0:08 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT02 | 4 | WTG | 20:35 | 20:44 | 0:09 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-05 | Gujarat | Sadla | SDLT02 | 4 | WTG | 16:39 | 16:47 | 0:08 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-05 | Gujarat | Sadla | SDLT02 | 4 | WTG | 16:50 | 16:54 | 0:04 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-05 | Gujarat | Sadla | SDLT02 | 4 | WTG | 17:08 | 17:12 | 0:04 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-09 | Gujarat | Sadla | SDLT02 | 4 | WTG | 19:06 | 20:51 | 1:45 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | Attend wtg and wtg for reduce power found ccu radiator motor mcb tirp checkckt found ok hold the mcb the start wtg
DJ Malpani - Sadla | 2021-04-10 | Gujarat | Sadla | SDLT02 | 4 | WTG | 12:05 | 15:55 | 3:50 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | Attend wtg and wtg for reduce power found ccu radiator motor mcb tirp checkckt found ok hold the mcb the start wtg
DJ Malpani - Sadla | 2021-04-11 | Gujarat | Sadla | SDLT02 | 4 | WTG | 7:51 | 24:00 | 16:09 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | WIP.
DJ Malpani - Sadla | 2021-04-12 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-13 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-14 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Stator breaker failed in closing when demanded to close.
DJ Malpani - Sadla | 2021-04-15 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Stator breaker failed in closing when demanded to close.
DJ Malpani - Sadla | 2021-04-16 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-17 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-18 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-19 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 15:59 | 15:59 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-19 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 15:59 | 16:22 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Feeder hand trip due to LV trip,Checked related circuit found Ok then charged feeder.
DJ Malpani - Sadla | 2021-04-19 | Gujarat | Sadla | SDLT02 | 4 | WTG | 16:22 | 24:00 | 7:38 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-20 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-21 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 9:30 | 9:30 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-21 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 9:30 | 9:39 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-21 | Gujarat | Sadla | SDLT02 | 4 | WTG | 9:39 | 24:00 | 14:21 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-22 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 6:48 | 6:48 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-22 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 6:48 | 7:00 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-22 | Gujarat | Sadla | SDLT02 | 4 | WTG | 7:00 | 10:48 | 3:48 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-22 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 10:48 | 17:02 | 6:14 | Internal shutdown | IG01 | Internal shutdown | Shutdown taken for DP Pole Phase to Phase line clearance work completed charged feeder.
DJ Malpani - Sadla | 2021-04-22 | Gujarat | Sadla | SDLT02 | 4 | WTG | 17:02 | 24:00 | 6:58 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so WTG is stop for material requierment (ACB)
DJ Malpani - Sadla | 2021-04-23 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 6:48 | 6:48 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attend & foundACB faulty so replaced new ACB mechanizam then reset turbine
DJ Malpani - Sadla | 2021-04-25 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:45 | 0:53 | 0:08 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-25 | Gujarat | Sadla | SDLT02 | 4 | WTG | 4:39 | 8:03 | 3:25 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | PLC Reboot than start WTG.
DJ Malpani - Sadla | 2021-04-26 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 7:54 | 7:54 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | PLC Reboot than start WTG.
DJ Malpani - Sadla | 2021-04-26 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 7:54 | 8:03 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-26 | Gujarat | Sadla | SDLT02 | 4 | WTG | 8:03 | 24:00 | 15:57 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-27 | Gujarat | Sadla | SDLT02 | 4 | WTG | 2:29 | 14:00 | 11:32 | Breakdown Maintenance | 4009 | Generator choke temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-27 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 19:52 | 21:43 | 1:51 | Feeder tripped E/F | IG02 | Earth Fault | LV trip due to feeder no 7 Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-28 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 19:14 | 19:50 | 0:36 | Feeder tripped O/C | IG03 | Over Current | Take trial than normally charge feeder.(Feeder Charged delay due to gusty Wind)
DJ Malpani - Sadla | 2021-04-28 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 21:24 | 21:52 | 0:28 | Feeder tripped O/C | IG03 | Over Current | Take trial than normally charge feeder.(Feeder Charged delay due to gusty Wind)
DJ Malpani - Sadla | 2021-04-28 | Gujarat | Sadla | SDLT02 | 4 | WTG | 22:15 | 24:00 | 1:45 | Breakdown Maintenance |  |  | After Feeder Charged Connectivity down (WIP)
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:00 | 3:03 | 3:03 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset delay due to SCADA Connectivity down Attend & reset from bottom.
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 19:53 | 20:29 | 0:36 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT02 | 4 | WTG | 20:29 | 21:36 | 1:07 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset delay due to SCADA Connectivity down Attend & reset from bottom.
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 21:36 | 21:46 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-05-02 | Gujarat | Sadla | SDLT02 | 4 | FORCE MAJEURE | 21:51 | 22:03 | 0:12 | Covid 19 | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-03 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 11:51 | 13:03 | 1:12 | Internal shutdown | IG01 | Internal shutdown | Shutdown taken for Pin insulator replacement work
DJ Malpani - Sadla | 2021-05-06 | Gujarat | Sadla | SDLT02 | 4 | FORCE MAJEURE | 13:04 | 13:16 | 0:12 | Covid 19 | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-09 | Gujarat | Sadla | SDLT02 | 4 | FORCE MAJEURE | 13:13 | 13:21 | 0:08 | Covid 19 | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-12 | Gujarat | Sadla | SDLT02 | 4 | WTG | 0:04 | 0:20 | 0:16 | Special Activity |  |  | Manual stop for Generator choke cooling fan replacement work, work completed then reset turbine
DJ Malpani - Sadla | 2021-05-15 | Gujarat | Sadla | SDLT02 | 4 | FORCE MAJEURE | 0:09 | 0:21 | 0:12 | Covid 19 | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-15 | Gujarat | Sadla | SDLT02 | 4 | GA INT | 9:36 | 17:02 | 7:26 | Internal shutdown |  |  | 220 KV line 1 and 2 shutdown for 220 kV substation maintenance work, work completed after feeder charged.
DJ Malpani - Sadla | 2021-05-16 | Gujarat | Sadla | SDLT02 | 4 | FORCE MAJEURE | 16:14 | 16:26 | 0:12 | Covid 19 | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-16 | Gujarat | Sadla | SDLT02 | 4 | FORCE MAJEURE | 17:45 | 17:57 | 0:12 | Covid 19 | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-18 | Gujarat | Sadla | SDLT02 | 4 | FORCE MAJEURE | 4:42 | 24:00 | 19:18 | Natural Calamity |  |  | 220KV line 1 & 2 trip due to Cyclone
DJ Malpani - Sadla | 2021-05-19 | Gujarat | Sadla | SDLT02 | 4 | FORCE MAJEURE | 0:00 | 16:22 | 16:22 | Natural Calamity |  |  | Cyclone stop after patrolling work done then PSS transformer charge after feeder charge normally.
DJ Malpani - Sadla | 2021-04-01 | Gujarat | Sadla | SDLT05 | 4 | WTG | 0:00 | 22:46 | 22:46 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Attend turbine and found torue limiter failure so replaced it then reset turbine
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT05 | 4 | WTG | 0:20 | 0:24 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT05 | 4 | WTG | 8:51 | 8:55 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT05 | 4 | WTG | 10:09 | 10:13 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT05 | 4 | WTG | 19:04 | 19:08 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT05 | 4 | WTG | 21:23 | 21:27 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-03 | Gujarat | Sadla | SDLT05 | 4 | WTG | 19:50 | 19:54 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-04 | Gujarat | Sadla | SDLT05 | 4 | WTG | 9:12 | 9:16 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-04 | Gujarat | Sadla | SDLT05 | 4 | WTG | 10:00 | 10:04 | 0:04 | Breakdown Maintenance | 3027 | Rotor brake accumulator pressure above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-06 | Gujarat | Sadla | SDLT05 | 4 | WTG | 15:54 | 19:04 | 3:10 | Breakdown Maintenance |  |  | Attend wtg and stator breaker releted ckt check and motor faulty so replace than start wtg.
DJ Malpani - Sadla | 2021-04-07 | Gujarat | Sadla | SDLT05 | 4 | WTG | 1:45 | 2:17 | 0:32 | Breakdown Maintenance |  |  | Attend wtg and ACB releted ckt check and no any about ckt fault so after than start wtg.
DJ Malpani - Sadla | 2021-04-07 | Gujarat | Sadla | SDLT05 | 4 | WTG | 10:40 | 10:44 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-07 | Gujarat | Sadla | SDLT05 | 4 | WTG | 10:51 | 10:55 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-07 | Gujarat | Sadla | SDLT05 | 4 | WTG | 12:01 | 12:05 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-07 | Gujarat | Sadla | SDLT05 | 4 | WTG | 13:40 | 16:52 | 3:12 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Attend wtg and ACB Mechnism stuck so rectification work completed than start wtg.
DJ Malpani - Sadla | 2021-04-09 | Gujarat | Sadla | SDLT05 | 4 | WTG | 9:38 | 16:10 | 6:32 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Attend wtg and ACB releted ckt check and no any about ckt fault so acb mechanizam replace after than start wtg.
DJ Malpani - Sadla | 2021-04-13 | Gujarat | Sadla | SDLT05 | 4 | WTG | 20:20 | 20:32 | 0:12 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-13 | Gujarat | Sadla | SDLT05 | 4 | WTG | 20:57 | 21:13 | 0:16 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-15 | Gujarat | Sadla | SDLT05 | 4 | WTG | 22:41 | 23:55 | 1:14 | Breakdown Maintenance | 12098 | Blade 3: Can Communication failure (Slave or Master not in operational state or Guarding error). | Blade 3: Can Communication failure (Slave or Master not in operational state or Guarding error).
DJ Malpani - Sadla | 2021-04-16 | Gujarat | Sadla | SDLT05 | 4 | WTG | 0:00 | 0:09 | 0:09 | Breakdown Maintenance | 12098 | Blade 3: Can Communication failure (Slave or Master not in operational state or Guarding error). | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-17 | Gujarat | Sadla | SDLT05 | 4 | WTG | 13:00 | 13:04 | 0:04 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-18 | Gujarat | Sadla | SDLT05 | 4 | WTG | 13:40 | 14:12 | 0:32 | Breakdown Maintenance | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-19 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 15:59 | 16:22 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Feeder hand trip due to LV trip,Checked related circuit found Ok then charged feeder.
DJ Malpani - Sadla | 2021-04-21 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 9:30 | 9:39 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-22 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 6:48 | 7:00 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-22 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 10:48 | 17:02 | 6:14 | Internal shutdown | IG01 | Internal shutdown | Shutdown taken for DP Pole Phase to Phase line clearance work completed charged feeder.
DJ Malpani - Sadla | 2021-04-25 | Gujarat | Sadla | SDLT05 | 4 | WTG | 17:02 | 17:06 | 0:04 | Breakdown Maintenance | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-25 | Gujarat | Sadla | SDLT05 | 4 | WTG | 17:39 | 20:26 | 2:47 | Breakdown Maintenance | 9083 | Gearbox oil offline filter feedback does not match demand. | PLC Reboot than start WTG.
DJ Malpani - Sadla | 2021-04-25 | Gujarat | Sadla | SDLT05 | 4 | WTG | 22:49 | 23:29 | 0:40 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-26 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 7:54 | 8:03 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-26 | Gujarat | Sadla | SDLT05 | 4 | WTG | 20:14 | 20:38 | 0:24 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-27 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 19:52 | 21:43 | 1:51 | Feeder tripped E/F | IG02 | Earth Fault | LV trip due to feeder no 7 Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-28 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 19:14 | 19:50 | 0:36 | Feeder tripped O/C | IG03 | Over Current | Take trial than normally charge feeder.(Feeder Charged delay due to gusty Wind)
DJ Malpani - Sadla | 2021-04-28 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 21:24 | 21:52 | 0:28 | Feeder tripped O/C | IG03 | Over Current | Take trial than normally charge feeder.(Feeder Charged delay due to gusty Wind)
DJ Malpani - Sadla | 2021-04-28 | Gujarat | Sadla | SDLT05 | 4 | WTG | 22:15 | 24:00 | 1:45 | Breakdown Maintenance |  |  | After Feeder Charged Connectivity down (WIP)
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT05 | 4 | WTG | 0:00 | 3:23 | 3:23 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset delay due to SCADA Connectivity down Attend & reset from bottom.
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 19:53 | 20:29 | 0:36 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT05 | 4 | WTG | 20:29 | 21:59 | 1:30 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset delay due to SCADA Connectivity down Attend & reset from bottom.
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 21:36 | 21:46 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-05-02 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 21:57 | 22:01 | 0:04 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-02 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 22:01 | 22:05 | 0:04 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-02 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 22:05 | 22:09 | 0:04 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-02 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 22:09 | 22:13 | 0:04 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-02 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 22:13 | 22:17 | 0:04 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-03 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 11:51 | 13:03 | 1:12 | Internal shutdown | IG01 | Internal shutdown | Shutdown taken for Pin insulator replacement work
DJ Malpani - Sadla | 2021-05-05 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 17:01 | 17:02 | 0:01 | Covid 19 | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-05 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 17:42 | 17:58 | 0:15 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | PLC Reboot than start wtg.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-07 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 18:09 | 18:13 | 0:04 | Covid 19 | 4018 | Stator breaker failed in closing when demanded to close. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-07 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 18:18 | 18:22 | 0:04 | Covid 19 | 4018 | Stator breaker failed in closing when demanded to close. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-07 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 19:02 | 19:06 | 0:04 | Covid 19 | 4018 | Stator breaker failed in closing when demanded to close. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-08 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 12:57 | 24:00 | 11:03 | ROW |  |  | Manual stop for security ROW.
DJ Malpani - Sadla | 2021-05-09 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | ROW |  |  | Manual stop due to security payment issue.
DJ Malpani - Sadla | 2021-05-10 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 0:00 | 9:39 | 9:39 | ROW |  |  | Security ROW resolved & Start turbine
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 2:02 | 2:06 | 0:04 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 2:06 | 2:10 | 0:04 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 2:10 | 2:14 | 0:04 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 2:14 | 2:18 | 0:04 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 2:18 | 2:37 | 0:19 | Covid 19 | 9083 | Gearbox oil offline filter feedback does not match demand. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 13:11 | 14:15 | 1:04 | Covid 19 | 12049 | Blade 1: Safety run is active. | PLC Reboot, than start WTG.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-15 | Gujarat | Sadla | SDLT05 | 4 | GA INT | 9:36 | 17:02 | 7:26 | Internal shutdown |  |  | 220 KV line 1 and 2 shutdown for 220 kV substation maintenance work, work completed after feeder charged.
DJ Malpani - Sadla | 2021-05-15 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 17:48 | 18:37 | 0:49 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-16 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 16:09 | 16:21 | 0:12 | Covid 19 | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-16 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 17:51 | 18:07 | 0:16 | Covid 19 | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-16 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 18:28 | 19:00 | 0:32 | Covid 19 | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-16 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 19:12 | 19:36 | 0:24 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-17 | Gujarat | Sadla | SDLT05 | 4 | WTG | 11:43 | 12:20 | 0:37 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-05-17 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 13:21 | 24:00 | 10:39 | Natural Calamity | 21064 | Emergency Button TB100 pressed | WIP. ( Not attend due to Cyclone Effect.)
DJ Malpani - Sadla | 2021-05-18 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 0:00 | 4:42 | 4:42 | Natural Calamity | 21064 | Emergency Button TB100 pressed | WIP. ( Not attend due to Cyclone Effect.)
DJ Malpani - Sadla | 2021-05-18 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 4:42 | 24:00 | 19:18 | Natural Calamity |  |  | 220KV line 1 & 2 trip due to Cyclone
DJ Malpani - Sadla | 2021-05-19 | Gujarat | Sadla | SDLT05 | 4 | FORCE MAJEURE | 0:00 | 16:22 | 16:22 | Natural Calamity |  |  | Cyclone stop after patrolling work done then PSS transformer charge after feeder charge normally.
DJ Malpani - Sadla | 2021-05-20 | Gujarat | Sadla | SDLT05 | 4 | WTG | 14:27 | 15:03 | 0:37 | Breakdown Maintenance | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-05-20 | Gujarat | Sadla | SDLT05 | 4 | WTG | 16:44 | 17:07 | 0:23 | Breakdown Maintenance | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT06 | 4 | WTG | 19:22 | 19:26 | 0:04 | Breakdown Maintenance | 1016 | Anemometer 2 measurement error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-02 | Gujarat | Sadla | SDLT06 | 4 | WTG | 19:39 | 19:43 | 0:04 | Breakdown Maintenance | 1005 | Anemometer 1 measurement error. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-07 | Gujarat | Sadla | SDLT06 | 4 | WTG | 16:34 | 16:38 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-13 | Gujarat | Sadla | SDLT06 | 4 | WTG | 18:54 | 19:10 | 0:16 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-18 | Gujarat | Sadla | SDLT06 | 4 | WTG | 19:34 | 19:46 | 0:12 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-19 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 15:59 | 16:22 | 0:23 | Feeder tripped E/F | IG02 | Earth Fault | Feeder hand trip due to LV trip,Checked related circuit found Ok then charged feeder.
DJ Malpani - Sadla | 2021-04-21 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 9:30 | 9:39 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-21 | Gujarat | Sadla | SDLT06 | 4 | WTG | 18:46 | 18:54 | 0:08 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-22 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 6:48 | 7:00 | 0:12 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-22 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 10:48 | 17:02 | 6:14 | Internal shutdown | IG01 | Internal shutdown | Shutdown taken for DP Pole Phase to Phase line clearance work completed charged feeder.
DJ Malpani - Sadla | 2021-04-25 | Gujarat | Sadla | SDLT06 | 4 | WTG | 17:03 | 20:04 | 3:00 | Breakdown Maintenance | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | PLC Reboot than start WTG.
DJ Malpani - Sadla | 2021-04-25 | Gujarat | Sadla | SDLT06 | 4 | WTG | 22:54 | 23:30 | 0:36 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-26 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 7:54 | 8:03 | 0:09 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-26 | Gujarat | Sadla | SDLT06 | 4 | WTG | 8:03 | 8:40 | 0:37 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Checked all related parameters found OK then reset turbine.
DJ Malpani - Sadla | 2021-04-27 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 19:52 | 21:43 | 1:51 | Feeder tripped E/F | IG02 | Earth Fault | LV trip due to feeder no 7 Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-28 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 19:14 | 19:50 | 0:36 | Feeder tripped O/C | IG03 | Over Current | Take trial than normally charge feeder.(Feeder Charged delay due to gusty Wind)
DJ Malpani - Sadla | 2021-04-28 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 21:24 | 21:52 | 0:28 | Feeder tripped O/C | IG03 | Over Current | Take trial than normally charge feeder.(Feeder Charged delay due to gusty Wind)
DJ Malpani - Sadla | 2021-04-28 | Gujarat | Sadla | SDLT06 | 4 | WTG | 22:15 | 24:00 | 1:45 | Breakdown Maintenance |  |  | After Feeder Charged Connectivity down (WIP)
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT06 | 4 | WTG | 0:00 | 3:03 | 3:03 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset delay due to SCADA Connectivity down Attend & reset from bottom.
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 19:53 | 20:29 | 0:36 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-04-29 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 21:36 | 21:46 | 0:10 | Feeder tripped E/F | IG02 | Earth Fault | Take trial than normally charge feeder.
DJ Malpani - Sadla | 2021-05-02 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 22:00 | 22:12 | 0:12 | Covid 19 | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-03 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 11:51 | 13:03 | 1:12 | Internal shutdown | IG01 | Internal shutdown | Shutdown taken for Pin insulator replacement work
DJ Malpani - Sadla | 2021-05-04 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 13:26 | 15:12 | 1:46 | Covid 19 | 4109 | CC101 fuse for cooling fans power supply is switched off or tripped. | Attend wtg check all ckt found fuse burn so replace fuse than start wtg
DJ Malpani - Sadla | 2021-05-05 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 16:04 | 16:05 | 0:01 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-05 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 16:45 | 16:46 | 0:01 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-06 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 16:17 | 16:36 | 0:19 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-06 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 16:40 | 16:51 | 0:12 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-06 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 16:56 | 17:17 | 0:21 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-06 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 17:33 | 17:57 | 0:24 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-07 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 0:01 | 1:27 | 1:26 | Covid 19 | 27007 | Converter water pump overload switch open/tripped. | Attend wtg found MPCB trip so check related connection then charge MPCB then start wtg(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-07 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 16:49 | 16:58 | 0:09 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-08 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 11:22 | 11:29 | 0:07 | Covid 19 | 21077 | SLC: Tower vibration switch tripped. | SLC: Tower vibration switch tripped.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-08 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 12:57 | 24:00 | 11:03 | ROW |  |  | Manual stop for security ROW.
DJ Malpani - Sadla | 2021-05-09 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | ROW |  |  | Manual stop due to security payment issue.
DJ Malpani - Sadla | 2021-05-10 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 0:00 | 9:53 | 9:53 | ROW |  |  | Security ROW resolved & Start turbine
DJ Malpani - Sadla | 2021-05-11 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 14:54 | 16:42 | 1:48 | Covid 19 | 26001 | All tower-vibration sensors in drivetrain direction defective | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-12 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 16:09 | 16:56 | 0:46 | Covid 19 | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-12 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 18:46 | 18:54 | 0:07 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 12:30 | 12:58 | 0:28 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 13:13 | 13:27 | 0:14 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 13:31 | 13:37 | 0:06 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 13:56 | 14:25 | 0:29 | Covid 19 | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 14:28 | 14:46 | 0:18 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 14:51 | 14:58 | 0:07 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 17:20 | 19:46 | 2:27 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 19:51 | 20:20 | 0:29 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 20:27 | 20:42 | 0:15 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-13 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 20:46 | 24:00 | 3:14 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 12:49 | 14:16 | 1:26 | Covid 19 | 4027 | Alarm that stator breaker control sequence state machine detected an error. | PLC Reboot, than start WTG.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 14:19 | 14:36 | 0:16 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 14:37 | 14:44 | 0:07 | Covid 19 | 21064 | Emergency Button TB100 pressed | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-14 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 15:23 | 15:28 | 0:05 | Covid 19 | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-15 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 3:14 | 3:18 | 0:04 | Covid 19 | 21077 | SLC: Tower vibration switch tripped. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-15 | Gujarat | Sadla | SDLT06 | 4 | GA INT | 9:36 | 17:02 | 7:26 | Internal shutdown |  |  | 220 KV line 1 and 2 shutdown for 220 kV substation maintenance work, work completed after feeder charged.
DJ Malpani - Sadla | 2021-05-16 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 17:29 | 17:56 | 0:27 | Covid 19 | 11007 | Power deviation delayed between power measurement device and converter above limit. | Checked all related parameters found OK then reset turbine.(Unable to attend machine as facing pandemic condition due to COVID-19 across globe and as per Government advisory free movement of people is restricted all over India.)
DJ Malpani - Sadla | 2021-05-18 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 4:42 | 24:00 | 19:18 | Natural Calamity |  |  | 220KV line 1 & 2 trip due to Cyclone
DJ Malpani - Sadla | 2021-05-19 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 0:00 | 16:22 | 16:22 | Natural Calamity |  |  | Cyclone stop after patrolling work done then PSS transformer charge after feeder charge normally.
DJ Malpani - Sadla | 2021-05-19 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 19:50 | 24:00 | 4:10 | Natural Calamity | 21093 | SLC is in not in operational mode. | Cyclone stop after Attend turbine SLC module faulty, material not available now turbine stop
DJ Malpani - Sadla | 2021-05-20 | Gujarat | Sadla | SDLT06 | 4 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | Natural Calamity | 21064 | Emergency Button TB100 pressed | Turbine u/b due to cyclone
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 2:05 | 24:00 | 21:55 | Breakdown Maintenance | 22010 | Speed measurement generator over-speed fast stop. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 22010 | Speed measurement generator over-speed fast stop. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 0:00 | 13:30 | 13:30 | Breakdown Maintenance | 22010 | Speed measurement generator over-speed fast stop. | Attended wtg, replace NGC then restored wtg.
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 12:05 | 12:13 | 0:08 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-07 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 13:07 | 13:19 | 0:12 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 12:11 | 12:15 | 0:04 | Breakdown Maintenance | 14010 | Hydraulic unit supply accumulator pressure sensor is defective (Short cut or wire break). | Error auto reset
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 12:12 | 12:28 | 0:16 | Breakdown Maintenance | 14010 | Hydraulic unit supply accumulator pressure sensor is defective (Short cut or wire break). | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 13:00 | 24:00 | 11:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 0:00 | 11:56 | 11:56 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 20:30 | 20:34 | 0:04 | Breakdown Maintenance | 14010 | Hydraulic unit supply accumulator pressure sensor is defective (Short cut or wire break). | Error auto reset
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT123 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 12:13 | 12:27 | 0:14 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-23 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 12:28 | 12:40 | 0:12 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 12:19 | 12:49 | 0:30 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT123 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 2:31 | 2:35 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Error auto reset
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT123 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 14:45 | 15:21 | 0:36 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT123 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 15:10 | 15:34 | 0:24 | Breakdown Maintenance | 21086 | SLC tiggered pitch safety run. | Reboot,reset after feeder charged & start WTG.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT123 | 3 | WTG | 2:50 | 2:54 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Error auto reset
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT123 | 3 | FORCE MAJEURE | 15:24 | 15:40 | 0:16 | COVID 19 | 14010 | Hydraulic unit supply accumulator pressure sensor is defective (Short cut or wire break). | Reboot,reset & start WTG..Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-05 | Gujarat | Savarkundla | SVRT123 | 3 | FORCE MAJEURE | 11:37 | 13:42 | 2:05 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT123 | 3 | FORCE MAJEURE | 13:41 | 13:45 | 0:04 | COVID 19 | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT123 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-11 | Gujarat | Savarkundla | SVRT123 | 3 | FORCE MAJEURE | 15:25 | 15:33 | 0:08 | COVID 19 | 14010 | Hydraulic unit supply accumulator pressure sensor is defective (Short cut or wire break). | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT123 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT123 | 3 | FORCE MAJEURE | 11:56 | 12:28 | 0:32 | COVID 19 | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT123 | 3 | FORCE MAJEURE | 15:39 | 16:05 | 0:26 | COVID 19 | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 8:52 | 8:56 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 12:40 | 13:00 | 0:20 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 4:56 | 13:20 | 8:24 | Breakdown Maintenance | 27006 | Converter cooling water pressure low alarm. | Attended wtg, converter coolent top-up then restored wtg.
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 17:47 | 17:55 | 0:08 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 14:35 | 14:39 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 20:16 | 20:24 | 0:08 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-11 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 12:54 | 12:58 | 0:04 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 13:21 | 13:25 | 0:04 | Breakdown Maintenance | 4027 | Alarm that stator breaker control sequence state machine detected an error. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 13:00 | 24:00 | 11:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 0:00 | 11:39 | 11:39 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 13:35 | 13:39 | 0:04 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 15:41 | 15:47 | 0:06 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT136 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 12:13 | 12:29 | 0:16 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-21 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 18:24 | 18:32 | 0:08 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-22 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 14:26 | 14:30 | 0:04 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 15:58 | 16:06 | 0:08 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 13:23 | 13:31 | 0:08 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT136 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 3:35 | 8:41 | 5:06 | Breakdown Maintenance | 10044 | Generator grounding brush worn error. | Attend & check error related circuit,found generator grounding brush worn out so replaced it with new one & restore WTG.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT136 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT136 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 15:10 | 15:30 | 0:20 | Breakdown Maintenance | 1024 | Wind direction difference error. | Reboot,reset after feeder charged & start WTG.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT136 | 3 | WTG | 14:53 | 15:05 | 0:12 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-05 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 17:14 | 17:22 | 0:08 | COVID 19 | 30001 | Yaw converter error is occurred. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 10:23 | 12:43 | 2:20 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 6:12 | 6:44 | 0:32 | COVID 19 | 30001 | Yaw converter error is occurred. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT136 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 15:15 | 16:04 | 0:49 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 15:38 | 15:42 | 0:04 | COVID 19 | 30001 | Yaw converter error is occurred. | Error auto reset
DJ Malpani - Savarkundla | 2021-05-10 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 15:05 | 18:34 | 3:29 | COVID 19 | 30011 | Hydraulic brake pressure reduced is out of range. | Attend & check error related circuit then reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-11 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 14:30 | 24:00 | 9:30 | COVID 19 | 23010 | Brake healthcheck timeout. | Attend & check error related circuit WIP.
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 0:00 | 12:59 | 12:59 | COVID 19 | 23010 | Brake healthcheck timeout. | Attend & check error related circuit & applied hydraulic system pressure accumulator then reboot ,reset & start WTG
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 15:52 | 16:03 | 0:11 | COVID 19 | 30001 | Yaw converter error is occurred. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 11:55 | 12:44 | 0:49 | COVID 19 | 14017 | Sensor of hydraulic unit supply pressure is defective (Short cut or wire break). | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT136 | 3 | FORCE MAJEURE | 6:55 | 7:00 | 0:05 | COVID 19 | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 13:27 | 13:39 | 0:12 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 12:45 | 16:27 | 3:42 | Breakdown Maintenance | 12006 | Health check error. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 15:12 | 15:20 | 0:08 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 17:19 | 17:23 | 0:04 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 13:00 | 24:00 | 11:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 0:00 | 11:49 | 11:49 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 12:48 | 13:00 | 0:12 | Breakdown Maintenance | 21086 | SLC tiggered pitch safety run. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT137 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 12:13 | 12:25 | 0:12 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-21 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 12:13 | 12:33 | 0:20 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Reboot & reset than start wtg.
DJ Malpani - Savarkundla | 2021-04-22 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 12:14 | 12:22 | 0:08 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 17:51 | 17:55 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-25 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 17:33 | 17:37 | 0:04 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT137 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 21:18 | 24:00 | 2:42 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Attended and WIP.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 0:00 | 10:10 | 10:10 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT137 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 14:45 | 24:00 | 9:15 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-04-30 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT137 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-03 | Gujarat | Savarkundla | SVRT137 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-05 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 14:40 | 14:40 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT137 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 15:15 | 24:00 | 8:45 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-10 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-11 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & found transformer faulty, required transformer ,awaiting for material.
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 11012 | Grid voltage is not OK. | Attend & replace transformer and charge transformer on no load condition & Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 9:15 | 9:52 | 0:37 | COVID 19 | 4018 | Stator breaker failed in closing when demanded to close. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT137 | 3 | FORCE MAJEURE | 10:40 | 14:42 | 4:02 | COVID 19 | 30009 | Maximum time for yaw positioning exceeded. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 16:40 | 17:02 | 0:22 | Breakdown Maintenance | 26009 | Offset of the tower-vibration sensor in drivetrain direction above error limit | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 12:49 | 14:09 | 1:20 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 0:54 | 0:58 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 16:54 | 16:58 | 0:04 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Error auto reset
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 14:00 | 14:40 | 0:40 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 14:47 | 14:59 | 0:12 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-07 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 16:55 | 16:59 | 0:04 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Error auto reset
DJ Malpani - Savarkundla | 2021-04-08 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 14:19 | 14:31 | 0:12 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 20:37 | 20:41 | 0:04 | Breakdown Maintenance | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Error auto reset
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 16:55 | 17:04 | 0:09 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-11 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 3:00 | 3:16 | 0:16 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 2:51 | 4:22 | 1:31 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | WTG Attended hard Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 13:00 | 24:00 | 11:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 0:00 | 11:40 | 11:40 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 12:15 | 17:15 | 5:00 | Breakdown Maintenance | 12044 | Blade 1: Blade angle greater allowed maximum. | Attend WTG,Check and found Pitch drive coupler loose, so tight it then restored WTG.
DJ Malpani - Savarkundla | 2021-04-17 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 15:24 | 15:32 | 0:08 | Breakdown Maintenance | 30013 | Hydraulic brake pressure sensors are defective. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 13:40 | 13:52 | 0:12 | Breakdown Maintenance | 26009 | Offset of the tower-vibration sensor in drivetrain direction above error limit | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT138 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 12:13 | 12:30 | 0:17 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-21 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 16:03 | 16:15 | 0:12 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Reboot & reset than start wtg.
DJ Malpani - Savarkundla | 2021-04-23 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 19:10 | 19:30 | 0:20 | Breakdown Maintenance | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 15:24 | 15:37 | 0:13 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-25 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 20:46 | 20:50 | 0:04 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Error auto reset
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 12:32 | 13:06 | 0:34 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT138 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT138 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 14:45 | 15:11 | 0:26 | Breakdown Maintenance | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-30 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 0:13 | 0:25 | 0:12 | Breakdown Maintenance | 30013 | Hydraulic brake pressure sensors are defective. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT138 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 15:10 | 15:18 | 0:08 | Breakdown Maintenance | 14006 | Hydraulic pump was running for too long time. | Reset after feeder charged & start WTG.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 8:01 | 8:13 | 0:12 | Breakdown Maintenance | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-03 | Gujarat | Savarkundla | SVRT138 | 3 | WTG | 14:00 | 15:34 | 1:34 | Preventive Maintenance |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-05 | Gujarat | Savarkundla | SVRT138 | 3 | FORCE MAJEURE | 1:12 | 1:16 | 0:04 | COVID 19 | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT138 | 3 | FORCE MAJEURE | 12:48 | 13:07 | 0:19 | COVID 19 | 30013 | Hydraulic brake pressure sensors are defective. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT138 | 3 | FORCE MAJEURE | 4:33 | 4:37 | 0:04 | COVID 19 | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT138 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT138 | 3 | FORCE MAJEURE | 15:15 | 15:31 | 0:16 | COVID 19 | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-11 | Gujarat | Savarkundla | SVRT138 | 3 | FORCE MAJEURE | 17:05 | 17:17 | 0:12 | COVID 19 | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT138 | 3 | FORCE MAJEURE | 6:51 | 7:15 | 0:24 | COVID 19 | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT138 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT138 | 3 | FORCE MAJEURE | 11:52 | 12:23 | 0:31 | COVID 19 | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT138 | 3 | FORCE MAJEURE | 18:25 | 18:33 | 0:08 | COVID 19 | 7739 | The Line side breaker feedback is not active when commanded to close. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 14:39 | 15:28 | 0:49 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 8:50 | 8:54 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 20:10 | 20:18 | 0:08 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 13:52 | 14:16 | 0:24 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 4:03 | 4:36 | 0:33 | Breakdown Maintenance | 25011 | External converter module task cycle execution error | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-07 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 14:22 | 14:37 | 0:15 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 8:47 | 8:57 | 0:10 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 15:22 | 15:26 | 0:04 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-11 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 12:37 | 12:49 | 0:12 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 20:35 | 20:59 | 0:24 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 13:00 | 24:00 | 11:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 0:00 | 11:24 | 11:24 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 22:47 | 22:51 | 0:04 | Breakdown Maintenance | 26009 | Offset of the tower-vibration sensor in drivetrain direction above error limit | Error auto reset
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 12:31 | 12:35 | 0:04 | Breakdown Maintenance | 26017 | More than 3 tower-vibration (acceleration peak-peak) warnings within specified time | Error auto reset
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT139 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-21 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 9:39 | 9:43 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Error auto reset
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 13:13 | 13:17 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Error auto reset
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT139 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 21:18 | 22:00 | 0:42 | Breakdown Maintenance | 23007 | Converter healthcheck alarm. | Reboot & reset than start WTG after feeder restored.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 9:21 | 9:25 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT139 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 14:45 | 15:03 | 0:18 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT139 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 4:50 | 4:55 | 0:05 | Breakdown Maintenance | 21086 | SLC tiggered pitch safety run. | Error auto reset
DJ Malpani - Savarkundla | 2021-05-03 | Gujarat | Savarkundla | SVRT139 | 3 | WTG | 11:40 | 13:20 | 1:40 | Preventive Maintenance |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT139 | 3 | FORCE MAJEURE | 13:19 | 13:55 | 0:36 | COVID 19 | 26017 | More than 3 tower-vibration (acceleration peak-peak) warnings within specified time | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT139 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-11 | Gujarat | Savarkundla | SVRT139 | 3 | FORCE MAJEURE | 16:12 | 16:32 | 0:20 | COVID 19 | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT139 | 3 | FORCE MAJEURE | 15:11 | 15:18 | 0:07 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT139 | 3 | FORCE MAJEURE | 11:49 | 12:18 | 0:29 | COVID 19 | 9035 | Gearbox oil filter 100% clogged. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT139 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 16:13 | 16:53 | 0:40 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 10:50 | 12:16 | 1:26 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 16:50 | 16:58 | 0:08 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 12:15 | 12:27 | 0:12 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-07 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 16:51 | 16:59 | 0:08 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-08 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 19:32 | 19:38 | 0:06 | Special Activity |  |  | WTG check AMC
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 12:23 | 12:30 | 0:07 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 16:51 | 16:55 | 0:04 | Breakdown Maintenance | 3029 | Rotor brake accumulator pressure below error limit. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 12:24 | 12:28 | 0:04 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 13:00 | 24:00 | 11:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 0:00 | 11:47 | 11:47 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-17 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 12:38 | 12:55 | 0:17 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 15:07 | 15:30 | 0:23 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 9:45 | 12:50 | 3:05 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Attended wtg check Error related circuit and clean yaw brake pad then After restart WTG.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT33 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-23 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 17:40 | 17:52 | 0:12 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-25 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 15:22 | 15:56 | 0:34 | Breakdown Maintenance | 22010 | Speed measurement generator over-speed fast stop. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 12:14 | 12:18 | 0:04 | Breakdown Maintenance | 3029 | Rotor brake accumulator pressure below error limit. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT33 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT33 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-30 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 13:30 | 13:50 | 0:20 | Breakdown Maintenance | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT33 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 15:53 | 15:57 | 0:04 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Error auto reset
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT33 | 3 | WTG | 11:58 | 12:04 | 0:06 | Breakdown Maintenance | 21086 | SLC tiggered pitch safety run. | Error auto reset
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT33 | 3 | FORCE MAJEURE | 15:13 | 15:17 | 0:04 | COVID 19 | 3029 | Rotor brake accumulator pressure below error limit. | Reboot,reset & start WTG..Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT33 | 3 | FORCE MAJEURE | 15:16 | 15:20 | 0:04 | COVID 19 | 3029 | Rotor brake accumulator pressure below error limit. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT33 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT33 | 3 | FORCE MAJEURE | 15:15 | 15:51 | 0:36 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT33 | 3 | FORCE MAJEURE | 12:19 | 12:23 | 0:04 | COVID 19 | 9045 | Gearbox oil input pressure below error limit. | Error auto reset
DJ Malpani - Savarkundla | 2021-05-10 | Gujarat | Savarkundla | SVRT33 | 3 | FORCE MAJEURE | 11:55 | 14:18 | 2:23 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT33 | 3 | FORCE MAJEURE | 13:57 | 14:09 | 0:12 | COVID 19 | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT33 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT33 | 3 | FORCE MAJEURE | 11:53 | 12:26 | 0:33 | COVID 19 | 9045 | Gearbox oil input pressure below error limit. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 13:16 | 13:45 | 0:29 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 8:42 | 8:58 | 0:16 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 17:06 | 18:08 | 1:02 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 16:50 | 16:58 | 0:08 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 10:02 | 10:06 | 0:04 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 18:11 | 18:27 | 0:16 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-07 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 13:32 | 13:52 | 0:20 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-08 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 10:02 | 10:10 | 0:08 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 18:12 | 18:20 | 0:08 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 17:01 | 17:09 | 0:08 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-11 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 10:07 | 10:11 | 0:04 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 18:12 | 18:16 | 0:04 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 13:00 | 24:00 | 11:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 0:00 | 11:28 | 11:28 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 16:33 | 16:55 | 0:22 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 16:00 | 16:21 | 0:21 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot & reset than start wtg.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT34 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-21 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 16:32 | 17:20 | 0:48 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot & reset than start wtg.
DJ Malpani - Savarkundla | 2021-04-23 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 12:11 | 12:19 | 0:08 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 6:46 | 6:54 | 0:08 | Breakdown Maintenance | 1024 | Wind direction difference error. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-25 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 20:53 | 21:26 | 0:33 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 11:45 | 11:53 | 0:08 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 10:45 | 12:21 | 1:36 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Attended wtg clean yaw brake pad then restored.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT34 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 1:47 | 1:51 | 0:04 | Breakdown Maintenance | 1024 | Wind direction difference error. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT34 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 15:23 | 15:31 | 0:08 | Breakdown Maintenance | 1024 | Wind direction difference error. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT34 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 15:28 | 15:32 | 0:04 | Breakdown Maintenance | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Error auto reset
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 20:01 | 20:40 | 0:39 | Breakdown Maintenance | 23010 | Brake healthcheck timeout. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-03 | Gujarat | Savarkundla | SVRT34 | 3 | WTG | 10:49 | 10:53 | 0:04 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Error auto reset
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT34 | 3 | FORCE MAJEURE | 15:11 | 15:35 | 0:24 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG..Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT34 | 3 | FORCE MAJEURE | 15:30 | 15:50 | 0:20 | COVID 19 | 30011 | Hydraulic brake pressure reduced is out of range. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT34 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT34 | 3 | FORCE MAJEURE | 11:05 | 13:28 | 2:23 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-10 | Gujarat | Savarkundla | SVRT34 | 3 | FORCE MAJEURE | 15:10 | 15:27 | 0:17 | COVID 19 | 30061 | Yaw converter is in state Error overload 2. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT34 | 3 | FORCE MAJEURE | 13:07 | 13:31 | 0:24 | COVID 19 | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT34 | 3 | FORCE MAJEURE | 11:00 | 11:18 | 0:18 | COVID 19 | 23010 | Brake healthcheck timeout. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT34 | 3 | FORCE MAJEURE | 11:48 | 12:10 | 0:22 | COVID 19 | 30001 | Yaw converter error is occurred. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT34 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT34 | 3 | FORCE MAJEURE | 13:38 | 13:42 | 0:04 | COVID 19 | 30001 | Yaw converter error is occurred. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | Attended wtg, and WIP.
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | WTG Attended checked error ralated circuit and Found one ACB faulti or torque limiter and generator encoder faulti. So awaiting for material
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | WTG Attended checked error ralated circuit and Found one ACB faulti or torque limiter and generator encoder faulti. So awaiting for material
DJ Malpani - Savarkundla | 2021-04-07 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | WTG Attended checked error ralated circuit and Found one ACB faulti or torque limiter and generator encoder faulti. So awaiting for material
DJ Malpani - Savarkundla | 2021-04-08 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | WTG Attended checked error ralated circuit and Found one ACB faulti or torque limiter and generator encoder faulti. So awaiting for material
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | WTG Attended checked error ralated circuit and Found one ACB faulti or torque limiter and generator encoder faulti. So awaiting for material
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | WTG Attended checked error ralated circuit and Found one ACB faulti or torque limiter and generator encoder faulti. So awaiting for material
DJ Malpani - Savarkundla | 2021-04-11 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 11:30 | 11:30 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 11:30 | 24:00 | 12:30 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-17 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 12:00 | 12:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT35 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 12:13 | 24:00 | 11:47 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-21 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-22 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-23 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-25 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 19:00 | 19:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT35 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 21:18 | 24:00 | 2:42 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 10:10 | 10:10 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | Material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT35 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 14:45 | 24:00 | 9:15 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | Material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-30 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 13:00 | 13:00 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | Attend & check error related circuit ,WIP
DJ Malpani - Savarkundla | 2021-04-30 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 14:36 | 24:00 | 9:24 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | Attend & check error related circuit ,WIP
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:00 | 10:26 | 10:26 | Breakdown Maintenance | 4033 | Stator breaker failed to open when demanded to open. | Attend & check error related circuit ,found connection problem in ACB so correct it then reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT35 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT35 | 3 | WTG | 0:46 | 0:56 | 0:10 | Breakdown Maintenance | 21086 | SLC tiggered pitch safety run. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 15:16 | 15:33 | 0:17 | COVID 19 | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reboot,reset & start WTG..Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-05 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 0:50 | 0:54 | 0:04 | COVID 19 | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 5:08 | 5:20 | 0:12 | COVID 19 | 9045 | Gearbox oil input pressure below error limit. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 15:18 | 15:26 | 0:08 | COVID 19 | 5034 | Nacelle cabinet +3NCA200 UPS module alarm. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 5:01 | 5:13 | 0:12 | COVID 19 | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT35 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 9:38 | 11:22 | 1:44 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-10 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 20:05 | 20:22 | 0:17 | COVID 19 | 9045 | Gearbox oil input pressure below error limit. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-11 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 2:47 | 2:51 | 0:04 | COVID 19 | 10037 | All sensors of generator bearing temperature NDE defective (Short cut or wire break). | error auto reset
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 3:44 | 4:04 | 0:20 | COVID 19 | 3029 | Rotor brake accumulator pressure below error limit. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 11:52 | 13:28 | 1:36 | COVID 19 | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT35 | 3 | FORCE MAJEURE | 10:09 | 10:10 | 0:01 | COVID 19 | 22009 | Speed measurement generator over-speed safety chain. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 12:14 | 12:34 | 0:20 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 8:52 | 8:56 | 0:04 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 10:30 | 11:34 | 1:04 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 15:35 | 15:47 | 0:12 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 9:00 | 10:02 | 1:02 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Attended wtg Reboot from laction, reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 12:59 | 13:14 | 0:15 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-07 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 15:13 | 15:21 | 0:08 | Breakdown Maintenance | 22011 | Speed measurement deviation between generator and rotor speed. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 14:13 | 15:10 | 0:57 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-11 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 9:19 | 9:40 | 0:21 | Breakdown Maintenance | 9045 | Gearbox oil input pressure below error limit. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 13:00 | 24:00 | 11:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 0:00 | 12:05 | 12:05 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 15:13 | 15:24 | 0:11 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 18:54 | 19:01 | 0:07 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT36 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 13:22 | 13:26 | 0:04 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Error auto reset
DJ Malpani - Savarkundla | 2021-04-21 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 13:42 | 13:52 | 0:10 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-22 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 13:24 | 13:32 | 0:08 | Breakdown Maintenance | 12090 | Blade 2: IPS not active in blade state STOP_OK. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 20:28 | 20:38 | 0:10 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT36 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 21:18 | 21:44 | 0:26 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot & reset than start WTG after feeder restored.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 4:13 | 5:51 | 1:38 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT36 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-30 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 13:58 | 14:12 | 0:14 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 12:29 | 12:57 | 0:28 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT36 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 15:10 | 15:22 | 0:12 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset after feeder charged & start WTG.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 12:44 | 13:30 | 0:46 | Breakdown Maintenance | 26017 | More than 3 tower-vibration (acceleration peak-peak) warnings within specified time | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-03 | Gujarat | Savarkundla | SVRT36 | 3 | WTG | 15:01 | 15:19 | 0:18 | Breakdown Maintenance | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 15:25 | 15:32 | 0:07 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG..Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-05 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 10:07 | 11:53 | 1:46 | COVID 19 |  |  | Manual stop for yaw pad cleaning & repeated error,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 23:30 | 23:34 | 0:04 | COVID 19 | 7666 | Positive 15V LS gate drive power supply under-voltage Fault. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 10:18 | 12:14 | 1:56 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT36 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 15:15 | 15:33 | 0:18 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 12:20 | 12:28 | 0:08 | COVID 19 | 9045 | Gearbox oil input pressure below error limit. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 1:38 | 2:25 | 0:47 | COVID 19 | 9045 | Gearbox oil input pressure below error limit. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 22:52 | 22:56 | 0:04 | COVID 19 | 7666 | Positive 15V LS gate drive power supply under-voltage Fault. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 11:55 | 12:36 | 0:41 | COVID 19 | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT36 | 3 | FORCE MAJEURE | 10:49 | 11:13 | 0:24 | COVID 19 | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 15:27 | 15:52 | 0:25 | Breakdown Maintenance | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 6:20 | 7:05 | 0:45 | Breakdown Maintenance | 21070 | SLC: Yaw control device twist protection switch tripped. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 15:53 | 16:13 | 0:20 | Breakdown Maintenance | 23010 | Brake healthcheck timeout. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 7:02 | 7:26 | 0:24 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-07 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 13:52 | 17:00 | 3:08 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Attended wtg check related circuit and clean yaw brake pad then After restart WTG.
DJ Malpani - Savarkundla | 2021-04-08 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 15:25 | 16:52 | 1:27 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Attended Hard Reboot & reset and start wtg. Late due to connectiviti lost.
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 14:54 | 14:58 | 0:04 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 12:42 | 12:50 | 0:08 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-11 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 14:45 | 15:00 | 0:15 | Breakdown Maintenance | 3029 | Rotor brake accumulator pressure below error limit. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 17:33 | 18:11 | 0:38 | Breakdown Maintenance | 30063 | Yaw converter is in state Error external fault. | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 12:47 | 24:00 | 11:13 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 0:00 | 11:31 | 11:31 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-17 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 15:38 | 15:52 | 0:14 | Breakdown Maintenance | 21070 | SLC: Yaw control device twist protection switch tripped. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 10:08 | 11:16 | 1:08 | Breakdown Maintenance | 14004 | Hydraulic unit oil level is too low. | Attend WTG, found hos Pipe leckage oil so tight or hydralic unit oil level low so topup oil then afetr stand restored the wtg
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 7:57 | 8:12 | 0:15 | Breakdown Maintenance | 11001 | Active power above limit. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT37 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-23 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 12:31 | 12:39 | 0:08 | Breakdown Maintenance | 3029 | Rotor brake accumulator pressure below error limit. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 9:45 | 10:00 | 0:15 | Breakdown Maintenance | 7733 | Converter system CAN handshake timeout exception. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-25 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 10:42 | 10:46 | 0:04 | Breakdown Maintenance | 7733 | Converter system CAN handshake timeout exception. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 12:35 | 12:45 | 0:10 | Breakdown Maintenance | 3029 | Rotor brake accumulator pressure below error limit. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT37 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 14:54 | 15:00 | 0:06 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT37 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 14:45 | 15:39 | 0:54 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Attend & reboot , reset then start WTG.
DJ Malpani - Savarkundla | 2021-04-30 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 17:44 | 17:53 | 0:09 | Breakdown Maintenance | 11001 | Active power above limit. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT37 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT37 | 3 | WTG | 15:10 | 15:46 | 0:36 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reboot,reset after feeder charged & start WTG.
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 2:57 | 5:57 | 3:00 | COVID 19 | 3029 | Rotor brake accumulator pressure below error limit. | Reboot,reset & start WTG..Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 16:51 | 16:55 | 0:04 | COVID 19 | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 15:45 | 15:53 | 0:08 | COVID 19 | 3029 | Rotor brake accumulator pressure below error limit. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 0:10 | 0:27 | 0:17 | COVID 19 | 11001 | Active power above limit. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 11:57 | 14:40 | 2:43 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT37 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 15:15 | 15:56 | 0:41 | COVID 19 | 6011 | TBC UPS module alarm. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 1:48 | 8:09 | 6:21 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Attend & check error related circuit then reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-11 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 0:36 | 1:40 | 1:04 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 2:05 | 2:27 | 0:22 | COVID 19 | 7733 | Converter system CAN handshake timeout exception. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 23:50 | 23:57 | 0:07 | COVID 19 | 7733 | Converter system CAN handshake timeout exception. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 11:17 | 11:49 | 0:32 | COVID 19 | 7733 | Converter system CAN handshake timeout exception. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT37 | 3 | FORCE MAJEURE | 8:23 | 8:54 | 0:31 | COVID 19 | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 6:10 | 24:00 | 17:50 | Breakdown Maintenance | 22010 | Speed measurement generator over-speed fast stop. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 22010 | Speed measurement generator over-speed fast stop. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 22010 | Speed measurement generator over-speed fast stop. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 2:00 | 24:00 | 22:00 | Breakdown Maintenance | 22010 | Speed measurement generator over-speed fast stop. | Attended wtg check and found Generator encoder faulty. So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 0:00 | 18:02 | 18:02 | Breakdown Maintenance | 22010 | Speed measurement generator over-speed fast stop. | Attended wtg check and found Generator encoder faulty. so replaced new one than after restored wtg (so encoder arrange svrt35)
DJ Malpani - Savarkundla | 2021-04-08 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 19:19 | 20:52 | 1:33 | Breakdown Maintenance | 14006 | Hydraulic pump was running for too long time. | Attended wtg error ralated check and hard reboot than start wtg.
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 14:21 | 14:30 | 0:09 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 15:40 | 15:48 | 0:08 | Breakdown Maintenance | 23010 | Brake healthcheck timeout. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-11 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 8:26 | 9:05 | 0:39 | Breakdown Maintenance | 26012 | Tower-vibration (acceleration peak-to-peak value) for drivetrain direction above error limit | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 16:47 | 16:51 | 0:04 | Breakdown Maintenance | 14006 | Hydraulic pump was running for too long time. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 12:30 | 24:00 | 11:30 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 0:00 | 12:04 | 12:04 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-17 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 13:06 | 13:12 | 0:06 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 22:20 | 22:35 | 0:15 | Breakdown Maintenance | 26009 | Offset of the tower-vibration sensor in drivetrain direction above error limit | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 15:11 | 16:23 | 1:12 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Attended wtg check Error related circuit and clean yaw brake pad then After restart WTG.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT67 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-21 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 14:21 | 14:25 | 0:04 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-23 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 12:19 | 12:39 | 0:20 | Breakdown Maintenance | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 17:30 | 17:34 | 0:04 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-25 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 15:02 | 15:23 | 0:21 | Breakdown Maintenance | 23010 | Brake healthcheck timeout. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 12:45 | 13:00 | 0:15 | Breakdown Maintenance | 28003 | Generator cooling water input temperature above error limit. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT67 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 8:32 | 8:50 | 0:18 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 3:34 | 3:49 | 0:15 | Breakdown Maintenance | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT67 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-30 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 7:00 | 7:12 | 0:12 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT67 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 15:10 | 15:22 | 0:12 | Breakdown Maintenance | 14006 | Hydraulic pump was running for too long time. | Reboot,reset after feeder charged & start WTG.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 12:03 | 12:24 | 0:21 | Breakdown Maintenance | 23010 | Brake healthcheck timeout. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-03 | Gujarat | Savarkundla | SVRT67 | 3 | WTG | 22:09 | 22:13 | 0:04 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Error auto reset
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 15:24 | 15:40 | 0:16 | COVID 19 | 26001 | All tower-vibration sensors in drivetrain direction defective | Reboot,reset & start WTG..Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-05 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 15:59 | 16:03 | 0:04 | COVID 19 | 14006 | Hydraulic pump was running for too long time. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 12:16 | 14:16 | 2:00 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 14:16 | 24:00 | 9:44 | COVID 19 | 4018 | Stator breaker failed in closing when demanded to close. | Attend & check error related circuit ,found ACB faulty.So required ACB & awaiting for material.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 0:00 | 13:46 | 13:46 | COVID 19 | 4018 | Stator breaker failed in closing when demanded to close. | Attend & replaced ACB arranged from location SVRT137 then restore WTG.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 18:34 | 24:00 | 5:26 | COVID 19 | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Attend & check error related circuit WIP.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 0:00 | 14:40 | 14:40 | COVID 19 | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Attend & check error related circuit WIP.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT67 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 15:15 | 24:00 | 8:45 | COVID 19 | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Attend & found torque limiter broken, so remove it & WIP.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Attend & check error related circuit WIP.
DJ Malpani - Savarkundla | 2021-05-10 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 0:00 | 21:04 | 21:04 | COVID 19 | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Attend & check error related circuit WIP.
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 11:54 | 12:07 | 0:13 | COVID 19 | 30011 | Hydraulic brake pressure reduced is out of range. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 19:29 | 19:33 | 0:04 | COVID 19 | 14006 | Hydraulic pump was running for too long time. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 11:55 | 12:33 | 0:38 | COVID 19 | 14006 | Hydraulic pump was running for too long time. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT67 | 3 | FORCE MAJEURE | 10:23 | 10:36 | 0:13 | COVID 19 | 7739 | The Line side breaker feedback is not active when commanded to close. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | WTG can not attend due to vehicle service stopped for payment issue .
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 0:00 | 18:00 | 18:00 | Breakdown Maintenance | 4018 | Stator breaker failed in closing when demanded to close. | Attended wtg, check& found UVR and charging motor faulty so replace then restored wtg.
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 12:52 | 12:56 | 0:04 | Breakdown Maintenance | 30009 | Maximum time for yaw positioning exceeded. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 9:35 | 10:25 | 0:50 | Breakdown Maintenance | 13001 | Pitch is started but the Capacitor State is not hysteresis Charge | Attended wtg check error related circuit it ok than reset and restored wtg.
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 13:17 | 13:24 | 0:07 | Breakdown Maintenance | 21086 | SLC tiggered pitch safety run. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-07 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 16:18 | 16:22 | 0:04 | Breakdown Maintenance | 7772 | Generator side synchronization timeout. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-08 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 19:55 | 20:55 | 1:00 | Breakdown Maintenance | 14010 | Hydraulic unit supply accumulator pressure sensor is defective (Short cut or wire break). | Attended wtg Reboot from laction, reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 13:08 | 13:20 | 0:12 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 16:53 | 17:05 | 0:12 | Breakdown Maintenance | 14008 | Hydraulic pump was switched on too many times during time period. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-11 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 12:28 | 12:44 | 0:16 | Breakdown Maintenance | 14010 | Hydraulic unit supply accumulator pressure sensor is defective (Short cut or wire break). | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-12 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 12:26 | 12:59 | 0:33 | Breakdown Maintenance | 23010 | Brake healthcheck timeout. | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 13:00 | 24:00 | 11:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 0:00 | 11:40 | 11:40 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 11:40 | 14:55 | 3:15 | Breakdown Maintenance | 14004 | Hydraulic unit oil level is too low. | Attended wtg checked error ralated circuit and,leckage from accumulator joint so tight or hydraulic oil top-up in than after restored wtg.
DJ Malpani - Savarkundla | 2021-04-17 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 11:55 | 11:59 | 0:04 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 14:50 | 14:58 | 0:08 | Breakdown Maintenance | 14010 | Hydraulic unit supply accumulator pressure sensor is defective (Short cut or wire break). | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT69 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-22 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 13:16 | 13:24 | 0:08 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-23 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 12:22 | 12:30 | 0:08 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 8:46 | 9:38 | 0:52 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reboot & reset than start wtg.
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 16:00 | 16:17 | 0:17 | Breakdown Maintenance | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT69 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 21:18 | 21:42 | 0:24 | Breakdown Maintenance | 24001 | Drive train swinging. | Reboot & reset than start WTG after feeder restored.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 11:39 | 11:49 | 0:10 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT69 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 15:02 | 15:14 | 0:12 | Breakdown Maintenance | 30011 | Hydraulic brake pressure reduced is out of range. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-30 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 12:09 | 12:15 | 0:06 | Breakdown Maintenance | 21064 | Emergency Button TB100 pressed | Error auto reset
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT69 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 20:18 | 20:26 | 0:08 | Breakdown Maintenance | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-03 | Gujarat | Savarkundla | SVRT69 | 3 | WTG | 12:48 | 12:56 | 0:08 | Breakdown Maintenance | 1023 | Wind speed difference error. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 15:26 | 15:42 | 0:16 | COVID 19 | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reboot,reset & start WTG..Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-05 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 9:47 | 11:42 | 1:55 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 16:05 | 16:16 | 0:11 | COVID 19 | 30011 | Hydraulic brake pressure reduced is out of range. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT69 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 12:20 | 12:44 | 0:24 | COVID 19 | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-11 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 19:25 | 19:37 | 0:12 | COVID 19 | 22012 | Speed measurement deviation delayed between generator and rotor speed. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 14:15 | 14:23 | 0:08 | COVID 19 | 14016 | Hydraulic unit supply pressure - accumulator pressure difference. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 13:40 | 24:00 | 10:20 | COVID 19 | 4018 | Stator breaker failed in closing when demanded to close. | Attend and check error relatrd cercuit and WIP
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 0:00 | 11:50 | 11:50 | COVID 19 | 4018 | Stator breaker failed in closing when demanded to close. | Attend and check error relatrd cercuit and WIP
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 11:55 | 24:00 | 12:05 | COVID 19 | 4018 | Stator breaker failed in closing when demanded to close. | Attend and check error relatrd cercuit and WIP
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT69 | 3 | FORCE MAJEURE | 0:00 | 24:00 | 24:00 | COVID 19 | 4018 | Stator breaker failed in closing when demanded to close. | Material required So awaiting for material.
DJ Malpani - Savarkundla | 2021-04-01 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 22:07 | 22:12 | 0:05 | Breakdown Maintenance | 9043 | Sensor of gearbox oil input pressure is defective (Short cut or wire break). | Error auto reset
DJ Malpani - Savarkundla | 2021-04-02 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 8:50 | 8:58 | 0:08 | Breakdown Maintenance | 7628 | The detected grid state from converter is faulted or not OK. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-03 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 8:18 | 8:22 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Reboot,reset & start WTG,Delay due to vehicle service stopped for payment issue.
DJ Malpani - Savarkundla | 2021-04-04 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 6:10 | 6:14 | 0:04 | Breakdown Maintenance | 30013 | Hydraulic brake pressure sensors are defective. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-05 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 13:11 | 13:35 | 0:24 | Breakdown Maintenance | 31042 | Yaw teeth lubrication is in maintenance state. | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-06 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 16:10 | 16:22 | 0:12 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reset & Start WTG
DJ Malpani - Savarkundla | 2021-04-09 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 13:52 | 13:56 | 0:04 | Breakdown Maintenance | 4142 | Stator breaker opened by undervoltage release because buffer not ready. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-10 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 7:28 | 7:32 | 0:04 | Breakdown Maintenance | 30013 | Hydraulic brake pressure sensors are defective. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-13 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 12:50 | 24:00 | 11:10 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-14 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-15 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 0:00 | 24:00 | 24:00 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-16 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 0:00 | 11:40 | 11:40 | Breakdown Maintenance |  |  | WTG manual stop due security vendor payment issue .
DJ Malpani - Savarkundla | 2021-04-17 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 20:31 | 21:02 | 0:31 | Breakdown Maintenance | 7614 | Converter system fault is active. | Reboot,Reset & Start WTG,
DJ Malpani - Savarkundla | 2021-04-18 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 7:17 | 7:50 | 0:33 | Breakdown Maintenance | 7614 | Converter system fault is active. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-19 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 16:34 | 17:07 | 0:33 | Breakdown Maintenance | 30001 | Yaw converter error is occurred. | Reboot & reset than start wtg.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT73 | 3 | GA INT | 12:00 | 12:13 | 0:13 | Feeder tripped E/F |  |  | Feeder - 03 33KV Line Y phase tripped in Earth fault.take trail and feeder normally charged.
DJ Malpani - Savarkundla | 2021-04-20 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 15:57 | 17:22 | 1:25 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Attend WTG,checked Error releted all CKT and connections, found that encoder cabll Damage, so replace cabll and start WTG.
DJ Malpani - Savarkundla | 2021-04-21 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 22:07 | 22:27 | 0:20 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Reboot & reset than start wtg.
DJ Malpani - Savarkundla | 2021-04-22 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 5:28 | 5:40 | 0:12 | Breakdown Maintenance | 7614 | Converter system fault is active. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-23 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 15:28 | 15:40 | 0:12 | Breakdown Maintenance | 7614 | Converter system fault is active. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-24 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 9:14 | 9:23 | 0:09 | Breakdown Maintenance | 7765 | Encoder rate of alarms exceeded treshold. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-25 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 5:48 | 5:52 | 0:04 | Breakdown Maintenance | 7765 | Encoder rate of alarms exceeded treshold. | Error auto reset
DJ Malpani - Savarkundla | 2021-04-26 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 3:37 | 3:49 | 0:12 | Breakdown Maintenance | 7765 | Encoder rate of alarms exceeded treshold. | Reboot,reset & start WTG.
DJ Malpani - Savarkundla | 2021-04-27 | Gujarat | Savarkundla | SVRT73 | 3 | GA INT | 19:00 | 21:18 | 2:18 | Feeder tripped E/F |  |  | Feeder-03 tripped in Earth fault . Take test trial, found everything normal then charged the feeder.
DJ Malpani - Savarkundla | 2021-04-28 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 17:06 | 24:00 | 6:54 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Reboot,reset & start WTG, Delay due to loss of connectivity.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 0:00 | 0:32 | 0:32 | Breakdown Maintenance | 14012 | Hydraulic unit supply accumulator pressure below error limit. | Attend & reboot , reset then start WTG.
DJ Malpani - Savarkundla | 2021-04-29 | Gujarat | Savarkundla | SVRT73 | 3 | GA INT | 10:10 | 14:45 | 4:35 | Internal shutdown |  |  | Feeder -03 LC taken for line maintenance & tree cutting work , after work done feeder charged.
DJ Malpani - Savarkundla | 2021-05-01 | Gujarat | Savarkundla | SVRT73 | 3 | GA INT | 15:05 | 15:10 | 0:05 | Feeder tripped E/F |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-02 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 14:20 | 14:28 | 0:08 | Breakdown Maintenance | 1024 | Wind direction difference error. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-03 | Gujarat | Savarkundla | SVRT73 | 3 | WTG | 5:50 | 6:02 | 0:12 | Breakdown Maintenance | 7766 | Encoder fault detection error persists. | Reset & start WTG.
DJ Malpani - Savarkundla | 2021-05-04 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 15:15 | 15:23 | 0:08 | COVID 19 | 21077 | SLC: Tower vibration switch tripped. | Reboot,reset & start WTG..Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-05 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 15:02 | 15:14 | 0:12 | COVID 19 | 30001 | Yaw converter error is occurred. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-06 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 0:20 | 0:28 | 0:08 | COVID 19 | 7614 | Converter system fault is active. | Reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-07 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 5:02 | 5:14 | 0:12 | COVID 19 | 7765 | Encoder rate of alarms exceeded treshold. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 4:35 | 4:39 | 0:04 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT73 | 3 | GA EXT | 14:40 | 15:15 | 0:35 | External Breakdown |  |  | After grid restored , SS & Feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-08 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 15:15 | 16:00 | 0:45 | COVID 19 | 21086 | SLC tiggered pitch safety run. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-09 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 13:45 | 13:57 | 0:12 | COVID 19 | 30001 | Yaw converter error is occurred. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-10 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 10:14 | 12:15 | 2:01 | COVID 19 |  |  | Manual stop for USS maintenance work,after work completed start WTG.
DJ Malpani - Savarkundla | 2021-05-11 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 17:43 | 17:55 | 0:12 | COVID 19 | 30001 | Yaw converter error is occurred. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-12 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 20:00 | 23:50 | 3:50 | COVID 19 | 30011 | Hydraulic brake pressure reduced is out of range. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.
DJ Malpani - Savarkundla | 2021-05-13 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 13:14 | 24:00 | 10:46 | COVID 19 | 23010 | Brake healthcheck timeout. | Attend and check error relatrd cercuit and WIP
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 0:00 | 12:24 | 12:24 | COVID 19 | 23010 | Brake healthcheck timeout. | Attend and check error relatrd cercuit and replace one relay than reboot ,reset &start WTG
DJ Malpani - Savarkundla | 2021-05-14 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 11:50 | 11:55 | 0:05 | COVID 19 |  |  | After checked current value take trial & feeder charged normally.
DJ Malpani - Savarkundla | 2021-05-15 | Gujarat | Savarkundla | SVRT73 | 3 | FORCE MAJEURE | 10:49 | 10:55 | 0:06 | COVID 19 | 7765 | Encoder rate of alarms exceeded treshold. | Reboot,reset & start WTG.Delay due to COVID-19 across the globe and as per Government advisory free movement of people is restricted all over India.